Survey 076, UPE, App A to E.       Final, 6 Jan 2004.

LIST OF APPENDICES

Page

A.  References and Bibliography				23

B. Assessment of the Main Campus Buildings		25

C. Assessment of the On-campus Residences		48

D. Assessment of the Sport Facilities 			56

E. Assessment of the Bird Street Campus 			61 - 64

-------------------------------------------------------------------------------------------------------------------

APPENDIX A:  REFERENCES AND BIBLIOGRAPHY

00 -  UPE Campus Map, by Z-CARD

01 - South Africa. Constitutional Assembly. 1996: The Constitution of the Republic of South Africa, (Act 108 of 1996). www.polity.org.za/govdocs/constitution/index.html

See also the Bill of Rights on www.sahrc.org.za/bill_of_rights.htm

02 - Human Rights Commission, November 2002:  Towards a barrier-free society: a report on accessibility and built environments.  45 page document available as 500k PDF file on www.gov.za/reports/2002/sahrc1.pdf

03 - HRC. November 2002:  Towards a barrier-free society – What every South African should know about disability rights.  37 page booklet that can also be downloaded from www.sahrc.org.za

04 - South Africa. 1997 : White Paper on an Integrated National Disability Strategy (INDS), Pretoria: Rustica Press.  see  http://www.polity.org.za

05 - Government of the Eastern Cape, December 2001: Office of the Status of Disabled Persons (OSDP), Integrated Provincial Disability Strategy (IPDS).

06 - South African Bureau of Standards. 1990: SABS 0400. Part S. Facilities for Disabled persons.

07 - South African Bureau of Standards. 1993: SABS 0246. Code of Practice. Accessibility of buildings to disabled persons.

08 - South African Department  of Trade and Industry. 18 April, 1986: National Building Regulations, Part S. Government Printer.

09 - The Occupational Health and Safety Act, 1993
10 - The Labour Relations Act, 1995
11 - The SA Qualifications Act, 1995
12 - The Basic Conditions of Employment Act, 1997
13 - The Employment Equity Act, 1998.  www.polity.org.za/govdocs/legislation/1998/act98-055.html

14 - The Code of Good Practice on Key Aspects of Disability in the Workplace,. See  www.labour.gov.za/docs/legislation/eea/codegoodpractise.htm   See also Ref 48 below.

15 - The Promotion of Equality and Prevention of Unfair Discrimination Act. (No 4 of 2000): www.gov.za/gazette/acts/2000/a4-00.pdf

16 - The Skills Development Act, 1998
17 - The Skills Development Levies Act, 1999
18 -  Dept of Education. White Paper 6, Special Needs Education. Building an Inclusive Education and Training System: www.polity.org.za/govdocs/white_papers/educ6.pdf

19- UCT Disability Unit, 2002: Physical Access and the UCT Built Environment. disable@humanities.uct.ac.za

20 - WITS. July 2002: Disability-Sensible Building Specifications and Guidelines for Physical Access on the Built and Natural Environment. www.wits.ac.za/tee/disability.htm#introduction

21 - Disabled People South Africa.  www.dpsa.org.za

22 - Cohen, Judy. 1998:  Disability Etiquette – Tips on interacting with people with disabilities. Eastern Paralysed Veterans Association, New York.  www.epva.org

23 - EPVA: Wheeling to Fire Safety. New York.  www.epva.org

24 - Chairman Industries. Undated. Grab Rails. Catalogue. 011-624 1222.

25 - Chapman, S. 1998:  Barrier-free Tourism in the Natural Environment for Peop[le with Physical Disability with Special Reference to East cape Facilities. Rhodes University. Unpublished Masters Thesis.

26 -  Durban Rotoract Club. 1996. Wheeling around Durban. Wasserfall.

27 - Filmer, R and J. 1998. Giving people with Disabilities the Opportunity to enjoy our Natural Heritage. Eco-Access. 011-477 3676. www.eco-access.org

28 - Harry, L and Sons. Wheeling Round East London: Wheelchair Access Guide. Ross Designs.

29 - Joubert, I et alia. Undated. Pretoria Accessibility Guide. Liason Committee for the Disabled.

30 - Morton, D. 1997: The Accessibility of Wheelchair Users in the Port Elizabeth Central Business District. UPE. Unpublished  Honours Treatise.

31 - Morton, D. 2000: An Investigation into wheelchair accessibility in the urban business districts of Port Elizabeth. UPE. Unpublished  Masters Thesis.

32 - Patton, C. 1995: The Disabled Community and National Parks. Unpublished honours dissertation, UCT.

33 - Theron, H.  1994: OFS Holiday Guide. Bloemfontein. Design Print

34 - Webb, AC. 2002:  Checklist for Access Surveys. 4 pages, unpublished. (Based on original sample from  Thompson, Seirlis and Cohen)

35 -  Webb, AC. 2003:  Basic Guidelines for Accessibility. 5 pages, unpublished. Based on SABS 0246, et alia. For a copy, email barndans@yebo.co.za

36 - Witte, C. 2000: Accessibility by the Physically Disabled, (with special reference to wheelchair users), to Hotels and their facilities along the Port Elizabeth Beachfront. PE Technikon. Unpublished dissertation for B Tech Degree in Tourism management.

37 – City Transport for People with Disabilities  (The Cape Town Dial-a-Ride System).

Press release by Afrikom dated 9 September 2002.   www.capetown.gov.za/press

Or contact Afrikom, 021-423 7263, or Joe Williams, Disability Desk, City of Cape Town 021-400-2764.

38 – Gradient Finder – a piece of equipment supplied by Peter Products, 011 787 1428

39 -  Lancaster University, UK. 1991 Guidance Notes for staff teaching students with special needs.

40 – Fanie du Toit (011-726 8040) et alia, 2003: A guideline on accommodating people with disabilities in the workplace.  NCPPDSA / Pricewaterhouse Coopers.

41 -  Fanie du Toit (011-726 8040) et alia, 2003: Training guide when assisting persons with physical disabilities in a restaurant.  NCPPDSA / Dulce’ Head Office.

42 -  Services SETA. 2003: Your guide to dealing with disability in the workplace. Part of an Employee Assistance Programme Toolkit.  www.serviceseta.org.za

43 – Dept of Public Works, 2001: Guideline for the design of accessible buildings. See www.publicworks.gov.za/documents/consultants

44 – CCMA (Commission for Conciliation, Mediation and Arbitration) : www.ccma.org.za

45 – Dept of Health. National Rehabilitation Policy. Nov 2000: Rehabilitation for All.

46 – PELIP Housing Company. 1999: Open the door for the disabled.

47 – Public Service Accountability Monitor. 2003: Know your rights. www.myrights.org.za

48 – Dept of Labour. 2003:  Technical Assistance Guidelines on the Employment of People with Disabilities.  www.labour.org.za

49 – The Promotion of Access to Information Act (No 2 of 2000): www.gov.za/gazette/acts.2000/a2-00.pdf

Footnote: In spite of  the wealth of information referred to above,  the key national standards on accessibility (Refs 06, 07 and 08)  are not freely available,  cannot be found on a  website and must be purchased from the relevant authority.

APPENDIX B:  ASSESSMENT OF THE MAIN CAMPUS BUILDINGS

The Main Campus was on a  confusing, multi-level site and included the main 20-story tower block and 17 other single to 5-story buildings.

The buildings  were assessed to determine any barriers that would prevent a disabled person from freely accessing the  buildings and facilities to study or work there. including disabled students, disabled employees, disabled suppliers, and  other disabled visitors.

##### SUMMARY

The  multi-level site was difficult to negotiate. Users of wheelchairs and other people with mobility problems found it particularly  arduous and time consuming to move between most areas. Extra time was needed to use lifts, compared with stairs

The 18 buildings were assessed but none were fully accessible.

Some of the upper floors were not served by lifts and were completely inaccessible.

There were no emergency evacuation procedures on display.

There were no signs to indicate accessible routes or facilities

Parking – there were many areas with no bays reserved for disabled people.

Ramps – all the buildings  had  one or more ramps, but most were too steep or too long for safe access by paraplegic wheelchair users.

Lifts – most  buildings had lifts but some were small and  difficult to enter. Many had  the top control too high to reach when seated in a wheelchair. None had Braille notation.

Doorways - many double doors were too narrow to get through in a wheelchair, unless both doors  were opened.

Toilets – only two of the 18 buildings had fully accessible paraplegic toilets.

Lecture Rooms – some had no space for wheelchairs due to fixed seating and sloping floors.

ATM’s and Pay Phones – all were too high to reach when seated in a wheelchair.

##### MAIN BUILDING: BLG 1

A 20-story building with a group of four lifts

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| GROUND FLOOR |  |
| Access from the walkway on the Guineafowl Road side was level through two tandem sets of double doors. Entrance was difficult through the manual doors, across soft rubber mats with in-line strips that were a hindrance to wheelchair users. | The tandem doors should be replaced by one or two sets of automatic sliding doors. The rubber mats should be replaced by ones with rubber strips across the direction of travel. |
| Access from the Taxi Rank down on Guineafowl Road was not possible because of 20 steps without handrails. | None at present. Taxis should be asked to drop disabled students in front of Blg 9, or other convenient point. |
| Access from the Cashier’s foyer in Blg 2 was hazardous down a steep tiled 1:7 ramp R1. There were no handrails and the surface was quite slippery. | This ramp should be rebuilt at 1:12 to the para spec. |
| Four lifts served the 20 floors. They did not meet the paraplegic spec in several respects - space not deep enough, top buttons too high, no Braille notation on controls. | The depth should be increased from 1050 to 1400 min, top buttons lowered from 1800 to 1200. Braille notation and audio annunciators should be fitted. |
| The M and F toilets on the GF are in a passages behind the lifts and are not accessible because the standard WC’s are too small and there are no paraplegic facilities. | None – see below |
| In the passage next to the F toilet is an unmarked door to a lobby leading to a well fitted unisex paraplegic toilet. The signage outside the passage is confusing, leading to one assuming that there is only an accessible toilet inside the F toilets, thus deterring some would be users. The door to the lobby is locked and the space inside is cluttered and appears to be used for storing cleaning materials and toilet rolls. The door to the paraplegic toilet has a strong door closer and a lock which is difficult to operate with weak fingers. | The sign outside the passage door should separate the Wheelchair and Female symbols. The door to the lobby should be removed to improve access to the door of the paraplegic WC. The lobby should be kept tidy and materials stored in the existing cupboards. The door closer should be removed from the door to the paraplegic WC and the door should be fitted with the correct handles and accessible lever lock. A bin should be provided for used paper towels |
| LOWER GROUND FLOOR: |  |
| The road under building has no access to post boxes, 150 up onto pavement. Only the lower rows of post boxes are accessible when seated in a wheelchair. | A 1:10 curb cut should be installed in the pavement. Wheelchair users should be allocated post boxes in the lower rows. |
| From the pavement there is a door through to the kiosk, switchboard and taxis, but path not accessible as rough and uneven concrete. | The path between the buildings should be made step-free. |
| From the pavement, the door into the Post Office is not accessible - 150 step up. | A 1:10 paraplegic ramp should be installed. |
| Distance Education: A 1:5 very steep ramp to the security gate and door prevent access. | A 1:10 paraplegic ramp should be installed. |
| Passage from lift lobby past M toilets ends with very steep 1:5 ramp through door to road. | 1:10 paraplegic ramp should be installed as this is an emergency exit. |
| M and F toilets are not accessible – no space in standard WC’s. | A unisex paraplegic toilet should be installed. |
| Printing Services: Level access from the lift, but narrow (730) door with strong closer difficult to negotiate, to small reception area with 1100 high counter. Printing workshop accessible but some machines too high to operate when seated. Back door has steep 1:8 ramp to road level. | Short term - call button should be installed outside door. Longer term – widen door and revise layout of reception area. Small ramps should be installed if future wheelchair user is employed to operate printing machines. 1:10 paraplegic ramp should be installed at back door. |
| Postal Services: There is a call button at 1200 high to call for assistance to enter through 770 door with closer. The clerk from the nearby Post Office counter will come through on request to serve wheelchair users at the Postal Services counter, 1200 high. | None at present |
| Post Office: Level access, 750 door with closer, passage past internal post boxes to the 1000 high service counter. | None at present. |
| KIOSK AND TOILET | Outside and under Blg 1 at LGF level. |
| The only access was via the lift to Blg 1 LGF, then via uneven paths to the kiosk. There was no access from the Taxi Rank and pavements from Blg 10 as the kiosk was 6 steps below road level. | The paths in the area should be made step-free. A 1:12 ramp should be installed between the Taxi Rank and the Kiosk. This would also provide a (albeit rather long, but undercover) route from the Taxi Rank, to the lifts in the LGF of Blg 1. |
| There was a semi-paraplegic Unisex Toilet adjacent to the Kiosk. It was locked with the key available only during the limited opening hours of the Kiosk. Several features were not to the paraplegic standard including – door lock difficult to operate, with no occupancy indicator or emergency release, door opening inwards, door closer should be removed, light switch too high, WC pan too low. | The toilet should be upgraded to the paraplegic standard. Disabled people should be able to access the toilet using their ID card or a remote/tag. |
| FIRST FLOOR: |  |
| From the lifts there is level access to the FF of the Conference Centre and Auditorium. | None |
| The M and F toilets on the FF are in a passages behind the lifts and are not accessible because the standard WC’s are too small and there are no paraplegic facilities. | None – see below |
| In the passage next to the F toilet is an unmarked door to a lobby leading to a well fitted unisex paraplegic toilet. The signage outside the passage is confusing, leading to one assuming that there is only an accessible toilet inside the F toilets. The door to the lobby is locked and the space inside is cluttered and appears to be used for storing cleaning materials and toilet rolls. The door to the paraplegic toilet has a strong door closer and a lock which is difficult to operate with weak fingers. | The sign outside the passage door should separate the Wheelchair and Female symbols. The door to the lobby should be removed to improve access to the door of the paraplegic WC. The lobby should be kept tidy and materials stored in the existing cupboards. The door closer should be removed from the door to the paraplegic WC and the door should be fitted with the correct handles and accessible lever lock. A bin should be provided for used paper towels. |
| FLOORS 2 to 18 |  |
| The M and F toilets on each floor were not accessible, the standard WC’s were too small and there were no paraplegic facilities. | Unisex paraplegic toilets should be installed on each floor. |
| Offices and lecture rooms were generally accessible. | Some reception areas and work stations may require minor modifications to accommodate disabled students or staff. |

##### CONFERENCE CENTRE (SENATE CHAMBER): BLG 2

A two-story building, linking Blg 9 and Blg 1 via ramps at GF level, served by the lifts in Blg 1..

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| The two steep 1:8 ramps (R2L or R2R) up from Blg 9 GF were not accessible. (Too steep, no handrails. Some of the slippery tiles on one ramp had been replaced by non-slip types). | The ramps should be modified to 1:12 paraplegic standards. |
| The steep 1:7 zig-zag ramp (R1) up from Blg 1 GF was not accessible. (Too steep, no handrails). | The ramps should be modified to 1:12 paraplegic standards. |
| There is no accessible toilet on GF of Blg 2. | None. The nearest unisex paraplegic toilet is in the passage behind the lifts on the GF of Blg 1. |
| Cashiers: The two service windows were too high for wheelchair users. It was difficult to get past door closers through the door into the small public space inside the enquiry office. | The windows should be lowered to 965. The layout inside the enquiry office should be made more accessible. |
| FIRST FLOOR |  |
| The lifts in Blg 1 give access to a level passage to the Senate Chamber foyer. | None |
| There is a FF unisex paraplegic toilet in the passage behind the lifts in Blg 1. | See Blg 1 above. |
| There is a 1:15 ramp (R2A) up to the Senate Chamber but it is hidden behind a glass brick wall, without an ISA sign. There is level space for several wheelchairs inside, in front of four tiers of seating. | An ISA sign should be installed to indicate the accessible route into the Senate Chamber. |

## CONFERENCE CENTRE ( AUDITORIUM): BLG 3

A two-story building linked to  Main Blg 1 at the GF and FF levels

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| From Blg 1 GF there is level access to the GF foyer at the back of the auditorium. The rear seats are not accessible as there were steps up to the auditorium. | None, the back of the auditorium can be accessed via the lift to the FF. |
| The payphone, 1750 high, is too high to be used when seated in a wheelchair. | The payphone should be lowered to 1200. |
| There is a GF unisex paraplegic toilet in the passage behind the lifts in Blg 1. | See Blg 1 above. |
| The slippery tiled ramp from the GF up to the mezzanine foyer was too steep at 1:6, and had no handrails. | The ramp should be modified to 1:12 paraplegic standards. |
| The refreshment counters in the mezzanine foyer were too high at 1100. | A section of the counters should be lowered to 950. |
| The carpeted ramp (R3) from the GF down to the lower, front level of the auditorium was too steep at 1:6, and had no handrails. | The ramp should be modified to 1:12 paraplegic standards. |
| The doors into the front of the auditorium were not accessible. (2x530 narrow doors with strong door closers to fight past, no hook backs) | The doors should be modified to give easy, clear 750 access. |
| There was no space inside for wheelchair users. | Some of the front seats should be removed, or be made removable as at the Starz Cinema, Boardwalk to provide space for wheelchair users. This feature should be mentioned when seats are being booked. |
| The steep 1:4 ramp (R3A) onto the stage was not accessible. (It was dangerously steep and had no handrails) | A 1:12 ramp to paraplegic standards should be provided. This could be a portable, modular construction. Alternatively a short-travel lift. |
| FIRST FLOOR: |  |
| The lifts in Blg 1 gave level access to the back (upper) entrance of the Auditorium but there was no space inside for wheelchair users. | Some of the rear seats should be removed, or be made removable as at the Starz Cinema, Boardwalk to provide space for wheelchair users. This feature should be mentioned when seats are being booked. |
| There is a FF unisex paraplegic toilet in the passage behind the lifts in Blg 1. | See Blg 1 above. |

## OLD MUTUAL LECTURE HALLS: BLG 4

A single-story building  that straddles Guineafowl Road.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| The nearest parking bays were outside Blg 9 GF, where there were 3 bays reserved for disabled people. | None . |
| There was access from Blg 9 via the lift to the FF, then level but difficult through 2 two sets of double doors to Blg 5. | The doors should be replaced by automatic sliding doors. |
| Access from Blg 6 GF was via a level passage, but difficult thru 2 x 680 narrow doors. | The doors should be replaced by automatic sliding doors. |
| Access from the covered walkway alongside of Blg 6 was up R4A, a 1: 8 ramp with a narrow 1000 wide landing at the top. This is also the entrance used after crossing the uncovered walkway across campus from Blg 7. | The ramp should be modified to 1:12 and the paraplegic spec. |
| The M and F toilets both had ‘paraplegic’ cubicles but there was no ISA signage and the cubicles were not to standard. The 1550x1550 was a too small, and fitted more like one for aged/frail people. The handrails were non-standard and too close to the pan, so obstructed access for a wheelchair user. The push-button flush was difficult to operate with a weak grip. There was no soap dispenser or hand drier. But the door lock was one of the best types. | Both cubicles should be modified to the full paraplegic standard. |
| G07, was a typical tiered lecture room with fixed seats and benches 720 under. The 1:10 ramped side aisle (R4) did not give safe access down to the front (Too steep, too long, no landings) The R and L back corner seats had been removed but the resulting 800 space was not sufficient for wheelchair users. | A level space of at least 1500 diameter should be provided at each side at the back, for wheelchair users. The rear bench should be raised to 750 under. |

##### SANLAM LECTURE HALLS: BLG 5

A single-story building that straddles Guineafowl Road.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| The nearest parking was outside the LGF of Blg 10 but none had been reserved for disabled people | Three 3500 paraplegic bays should be installed close to the entrance to Blg 10. The reserved bays and the route to the entrance should be under cover. |
| Access from Blg 10 was by lift to the FF, then was level, but difficult through a 900+500 door with stiff closer. | The door closer should be adjusted for less pressure. |
| Access from Blg 7 GF was up a 1:10 ramp (R5) and 2x700 double doors. | None at present. |
| The M and F toilets both had ‘paraplegic’ cubicles but there was no ISA signage and the cubicles were not to standard. The 1550x1550 was a too small, and fitted more like one for aged/frail people. The handrails were non-standard and too close to the pan, so obstructed access for a wheelchair user. The push-button flush was difficult to operate with a weak grip. There was no soap dispenser or hand drier. But the door lock was one of the best types. | Both cubicles should be modified to the full paraplegic standard. |
| G07, was a typical tiered lecture room with fixed seats and benches 720 under. The 1:10 ramped side aisle (R5A) did not give safe access down to the front (Too steep, too long, no landings) The R and L back corner seats had been removed but the resulting space was not sufficient for wheelchair users. | A level space of at least 1500 diameter should be provided at each side at the back, for wheelchair users. The rear bench should be raised to 750 under. |

EDUCATION: BLG 6

A three-story building with a lift

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| The nearest parking area was outside the back of Blg 11. | See below for recommendations to improve parking outside Blg 11. |
| Alternatively there were reserved parking bays outside Blg 9 but they were three times as far away, and required the use of the lift in Blg 9. | See below for recommendations to improve parking outside Blg 9 |
| Access from Blg 4 was via a level passage, but difficult thru 2 x 680 narrow doors into the GF. | The doors should be replaced by automatic sliding doors or a single door 900 wide. |
| Access from Blg 7 was across campus via an open walkway, up a steep 1:8 ramp R4A with a narrow landing, to the above narrow doors. | Ramp R4A should be modified to 1:12 and the paraplegic spec as recommended under Blg 4 above. |
| Access from Blg 14, the Kraal , was up a two-section ramp, bottom section R6, 1:15, 15m long, no landing until turn, top section R6A, 1:12, 20m long no landing until top, then 2 x 840 doors to LGF foyer. | None at present as the gradients are within spec, but the ramps are very long and tiring. Needs signage top and bottom. |
| Access from Blg 11, FF, Human Movement Science, was via a covered walkway to the LGF foyer. | None. |
| A lift served the three floors. It did not meet the paraplegic spec in several respects - space not deep enough, top buttons too high, no Braille. | The depth should be increased from 1140 to 1400 min, top buttons lowered from 1500 to 1200. Braille notation and audio annunciators should be fitted. |
| LOWER GROUND FLOOR |  |
| The M and F toilets were not accessible - standard cubicles, no space or fittings. | A unisex paraplegic toilet should be installed on the LGF. |
| Some lecture rooms/computer labs had loose tables or benches too low for wheelchair users. | At least some of the tables/benches should be available with 750 knee space. |
| Some lecture rooms (eg LG05) had fixed seating but no space for wheelchair users. | A 1500 diam space should be cleared at the back corners of the room , behind a bench with 750 knee space. |
| GROUND FLOOR |  |
| The M and F toilets were not accessible - standard cubicles, no space or fittings. | A unisex paraplegic toilet should be installed on the GF. |
| The offices and lecture rooms were generally accessible. | None |
| FIRST FLOOR |  |
| The M and F toilets were not accessible - standard cubicles, no space or fittings. | A unisex paraplegic toilet should be installed on the FF. |

MATHS & PSYCHOLOGY: BLG 7

A four-story building with a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were 2 wide parking bays reserved for disabled people amongst to other bays, about 30m from the LGF entrance at the Kraal end of Blg 7. It was dangerous for disabled people to negotiate traffic in the car park to reach the entrance. The signage was not to the paraplegic standard. There was a shallow 1:20 slope down from the parking area to the doors | Two or more 3500 wide paraplegic bays should be installed at a safer position close to the entrance. The reserved bays and the route to the entrance should be under cover. |
| At the Blg 5 end of the parking area, there was a a steep 1:7 ramp in the curb between the tarmac and an uneven concrete path to the entrance. | The ramp and path should be improved to the paraplegic spec. |
| There was access up from Guineafowl Road via two steep 1:9 ramps. | None at present, but upgrading should be considered in future as this offers the shortest rout to the taxi ranks. |
| There was level access from Blg 5 via a wide passage to very narrow 2 x 570 doors into the GF. | The doors should be replaced by automatic sliding doors or a single door 900 wide. |
| There was an alternative access from Blg 5 down ramp R5, 1:10, 10 m long, to the walkway past Blg 7, then up ramp R7, 1:12 , 12 m long, to the GF lift foyer. | None at present, but both these ramps should be upgraded to the paraplegic spec in future. |
| There was access from Blg 6 via an open walkway across campus then up ramps at either end of Blg 7, as described above. | None. |
| There was vehicle access from Kiewet Rd/Kraal level up a very steep 1:6 ramp R7A, 15m long, no landings, to LGF foyer. This ramp is dangerous and not acceptable for wheelchair users. | A lift should be installed between Blg 14 Kraal GF and FF, with a pedestrian walkway/ramp to link Blg 14 FF to Blg 7 LGF. |
| A lift served the four floors. It did not meet the paraplegic spec in several respects - space not deep enough, top buttons too high, no Braille. There were confusing level numbers, -1, 0, 1, 2, instead of LGF, GF, FF, 2F. | The depth should be increased from 1140 to 1400 min, top buttons lowered from 1500 to 1200. Braille notation and audio annunciators should be fitted. The buttons and floors should be marked with the standard LGF, GF, FF, 2F |
| LOWER GROUND FLOOR (-1) |  |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the LGF. |
| Narrow 2 x 630 doors prevented independent access to the corridor to the lecture rooms. | The doors should be replaced by automatic sliding doors or a single door 900 wide. |
| GROUND FLOOR (0) |  |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the GF. |
| From the GF foyer there were steps down to the mezzanine floor. The Head of Media Services, and the graphics section were therefore not accessible. | Access to this section should be investigated. |
| FIRST FLOOR (1) |  |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the FF. |
| SECOND FLOOR (2) |  |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the 2F. |
| Narrow 2 x 630 doors prevented independent access to the corridor to the lecture rooms. | The doors should be replaced by automatic sliding doors or a single door 900 wide. |

LIBRARY : FRONT OF BLG 8

A four-story building with two lifts. One lift  served the  floors occupied by the Library. The front of the LGF (basement) and the whole of the Ground and First floors were occupied by the Library. Other parts of the building were occupied by the  Architectural Depts and served by the other lift - see below.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| The nearest parking was outside Blg 7 LGF. Then via lift from LGF to GF, to the forecourt in front of the library. | None |
| If improved parking is installed by Blg 11 as recommended above, access by an alternative but longer route would be possible through Blg 11 to Blg 6 LGF, up the lift to GF, and on to the forecourt in front of the Library. | See recommendation above for improved parking for Blg 11 and Blg 6. |
| Alternatively, there is parking on the extension to Bushbuck Road, outside the Architectural Dept. Access to the Library would then be down the ramp to Architectural LGF level, then by key access through the lift to the Library LGF, or via the lift to other floors. | Disabled people should be issued with keys or tags/remote controls for the lifts to be able to navigate around the Library. |
| The only access from the forecourt in front of the Library was via two very steep ramps up to the landing in front of main door. (R8, 1:5, on the LHS; R8A, 1:7 on the RHS). | The two very steep ramps should be removed and replaced by a zig-zag 1:12 paraplegic ramp. |
| Two lifts served the four floors but access to various floors required the use of a key. The lifts did not meet the paraplegic spec in several respects including - space not deep enough, top buttons too high, no Braille. | The depth should be increased from 1250 to 1400 min, top buttons lowered from 1400 to 1200. Braille notation and audio annunciators should be fitted. |
| LOWER GROUND FLOOR (Basement) | (Books and function rooms) |
| The lifts are well hidden thru a maze of corridors, no signage. | Clear signs should be installed to indicate the position of the lift from all parts of the LGF. |
| The 750 wide aisles between book shelves were too narrow for wheelchair users. Only the bottom three of the seven shelves were within reach [<1200] | Aisles should be increased to 1500. Library staff and volunteers should be trained to assist disabled people to browse and retrieve books. |
| Auditorium - access through the 2x630 doors was only possible if both doors were open. | The double doors should be replaced by a 900 door, with a hinged side panel if required. |
| The auditorium was level but the aisles were only 750 wide between fixed seating. Some of the rear seats had been removed but the space was too cramped for wheelchair users. | The width of the aisles should be increased to 1500. 1500 diameter spaces should be cleared for wheelchair users, |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the GF. |
| ##### GROUND FLOOR | Admin, indexes and study facilities. |
| A 1000 wide Main entrance door gave access to the outer foyer with loose benches for refreshments. | None. |
| There was easy access to the Bookmarket through 2x 1000 manual sliding doors. Sells books and refreshments. | None. |
| The In and Out security passages to the library main foyer were 1000 wide with booms easy to push aside. | None |
| The lift was behind the Service Counters, no signage. | Clear signs should be installed to indicate the position of the lift from all parts of the GF, particularly when entering the front entrance.. |
| The Library main foyer had a carpeted floor. Carpet is often difficult to wheel across. | TBA |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the GF. |
| The study stations and the tables in the Study Room are too low (670 under) for wheelchair users. | At least some of the study stations and tables should be raised to 750 under. |
| In the Catalogue Room the top rows of index drawers (1400 high) cannot be reached when seated. | ?? Surely this info is being computerised. |
| Acquisitions and Sales sections at rear, access thru lift. | None |
| FIRST FLOOR | Mainly books. |
| The lift was not clearly signed. | Clear signs should be installed to indicate the position of the lift from all parts of the FF. |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. There was a separate M toilet which had some paraplegic features. | The existing M semi- paraplegic toilet should be upgraded to unisex status and signed accordingly. |
| The 750 wide aisles between some of the book shelves were too narrow for wheelchair users. Only the bottom three of the seven shelves were within reach [<1200] | Aisles should be increased to 1500. Library staff and volunteers should be trained to assist disabled people to browse and retrieve books. |
| The benches in the CD/Internet area were too low at 640 under. | At least some of the benches should be raised to 750 under. |

ARCHITECTURAL DEPARTMENTS: REAR OF BLG 8

The Architectural Departments occupy the rear  of the LGF  and the whole of the Second Floor and were served by one of the lifts.

There was an attic on top of the rear part of the  2F, occupied by the Construction Engineering and Quantity Surveying Depts, but there was no lift to the attic.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were no parking bays near the entrance. Parallel parking appeared to be practiced along the extension to Bushbuck Road. This is dangerous for disabled drivers who have to alight into the traffic flow. From the road level there was a very steep 1:6 ramp down to the entrance. | Paraplegic parking bays should be installed close to and the same level as the LGF entrance, with a max 1:12 road connecting with Bushbuck Road. |
| The nearest designated parking was the visitors parking on the grass off Bushbuck Rd, about 100m away, behind Blg 13. Bushbuck Road continued up paved ramp R13B, 1:7, 14m long, no landings, to the road alongside Blg 8. | This is totally unacceptable for disabled persons. |
| There was no access from the Library forecourt except down two very steep vehicle ramps, R8B, 1:6, 4m long, and R8C, 1:5, 8m long to Bushbuck Road. These ramps are too dangerous even for electric wheelchairs. | Wheelchair users should be prohibited from using these two ramps. An alternative route at maximum 1:12 should be installed between the Library forecourt and the LGF of the Architectural Dept. |
| There was limited access from the road level, down a steep ramp R8F, 1:6, 1400 wide, 6m long, walls without hand rails, to the LGF entrance. | Dependent on how paraplegic parking is to be provided, it may be necessary to replace the 1:6 ramp by a zig-zag ramp at 1:12. |
| LOWER GROUND FLOOR |  |
| Main Entrance by 2 x 1150 manual sliding doors with 60 step. Level access from the foyer to the lecture rooms and lifts. | The step should be bevelled at 1:10, and the doors should be automated. |
| Only one of the lifts could be entered from the foyer and it was programmed to serve only the LGF and FF. It did not reach the QS and Constr Eng attic. It did not meet the paraplegic spec in several respects including - space not deep enough, top buttons too high, no Braille. | The depth should be increased from 1140 to 1400 min, top buttons lowered from 1500 to 1200. Braille notation and audio annunciators should be fitted. |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the LGF. |
| NB: The Ground and First Floors of the building were occupied by the Library. |  |
| SECOND FLOOR |  |
| There were M and F toilets off the lift foyer. The M toilet was not accessible, – standard WC cubicles with no space or fittings. An attempt had been made to make the F toilet accessible by moving an internal wall to enclose both WC pans in one cubicle 1700 wide x 1600 deep. Very Chummy?. Several other features did not comply with the paraplegic spec. | A unisex paraplegic toilet should be installed on the 2F. |
| The double security doors into the Architectural Dept were not accessible, as the space inside was only 570 x 570. | An accessible entrance should be provided |
| There was a 40 high sill to the sliding door to the Reception, which had a 1150 high counter. Open plan to other parts of department. | The door sill should be bevelled at 1:10. At least 1000 wide section of the counter should be lowered to 950. |
| ATTIC ABOVE FF - The offices and lecture rooms of the Construction Management and Quantity Surveying departments were not accessible. They were in an attic above the Second floor, accessible only by a staircase. | ?? |

EMBIZWENI: BLG 9

A four-story building with a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were three wide parking bays reserved for disabled people about 50 m from the main GF entrance to BLG 9. The signage was not to the paraplegic standard. | Three 3500 paraplegic bays should be installed closer to the entrance. The reserved bays and the route to the entrance should be under cover. |
| There was a wide low gradient paved paths R9, 1:20, 30m long, to a wide ramp R9A, 1:15, 9m long, up to the entrance door to GF. Total distance about 50m. | None, see above. |
| There were two steep 1:8 ramps (R2L or R2R) between Blg 2 (Cashiers) and Blg 9 GF . These were not to the paraplegic spec - too steep, no handrails. Some of the slippery tiles on one ramp had been replaced by non-slip types). | The ramps should be modified to 1:12 paraplegic standards. |
| There were automatic sliding doors which gave level access from the GF to the walkway in front of the GF of Blg 1. There were bristle mats which were hard to cross in a wheelchair. | The bristle mats should be replaced by ones with rubber inserts across the direction of travel. |
| There was also direct access into the LGF and FF of the building – see below. |  |
| A lift served the four floors. It was in a passage off the main corridor, there were no overhead signs. The lift had no handrails. The buttons had no Braille notation. | Overhead signs should be installed on all floors. Handrails at 900 high, and Braille notation and audio annunciators should be fitted in the lift. |
| LOWER GROUND FLOOR |  |
| There was a restricted parking area P9A, below the building, with level access into the LGF foyer. The lift was in a passage off the foyer. There were no toilets in this part of the LGF. | This should be considered as a site for alternative reserved parking for disabled people. |
| HEALTH CLINIC. |  |
| The clinic was in a part of the LGF on the other side of the tunnel road from the parking and lift foyer. Access was difficult from inside the LGF. There was a bell push near the side door and lift for wheelchair users to signal the Health Clinic for assistance to exit the door, descend a 1:10 ramp and cross the tunnel road. There was then a 1:10 up to the clinic door. The clinic included a unisex toilet T9C, with a roll-in shower. | The clinic should be relocated to a more accessible and central part of the campus. Alternatively, or in addition, there should be restrooms for disabled people at strategic points around the campus. Some disabled people are incontinent and may need urgent access to toilet and clean-up facilities. |
| GROUND FLOOR |  |
| For direct access routes, see above. There was reasonable access to the departments on the GF. | None |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | None |
| There was a separate unisex paraplegic toilet. There was no overhead signage to indicate the position. The layout of the fittings was satisfactory and the toilet was large enough for the door to swung in and out for the convenience of disabled people who had limited hand function. The door had a small bolt which was difficult to operate, no occupancy signal or emergency release. | The unisex paraplegic toilet should be upgraded to the full paraplegic spec, including overhead signs. The door should not be fitted with a Door closer. There should be a swing-over type of handle/lock with occupancy signal and emergency release. If it is necessary to control access, disabled people should be able to use their ID tags etc. |
| FIRST FLOOR |  |
| There was direct and level access from Blg 4 but this was difficult through 2 two sets of double doors. | The doors should be replaced by automatic sliding doors. |
| There was reasonable access to the departments on the FF. | None. |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | None. |
| There was a separate unisex paraplegic toilet. There was no overhead signage to indicate the position. The layout of the fittings was satisfactory. The door was locked the key was kept in Room 105 opposite. The door had a very strong door closer. The lock had a small knob, no indicator and no emergency release. | The unisex paraplegic toilet should be upgraded to the full paraplegic spec, including overhead signs. The door should not be fitted with a door closer. There should be a swing-over type of handle/lock with occupancy signal and emergency release. If it is necessary to control access, disabled people should be able to use their ID tags etc. |
| SECOND FLOOR |  |
| There was reasonable access to the departments on the 2F. |  |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | None |
| There was a separate unisex paraplegic toilet. There was no overhead signage to indicate the position. The door was locked and there was no info about the key. | The unisex paraplegic toilet should be upgraded to the full paraplegic spec, including overhead signs. The door should not be fitted with a door closer. There should be a swing-over type of handle/lock with occupancy signal and emergency release. If it is necessary to control access, disabled people should be able to use their ID tags etc. |

MUSIC: BLG 10

A three-story building with a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| The were parking bays outside Blg 10 LGF, but none were reserved for disabled people. | Three 3500 paraplegic bays should be installed close to the entrance. The reserved bays and the route to the entrance should be under cover. |
| A lift served the three floors. It did not meet the paraplegic spec in some respects - top buttons too high, no Braille. | The top buttons should be lowered from xxxx to 1200. Braille notation and audio annunciators should be fitted. |
| LOWER GROUND FLOOR |  |
| There was reasonably level access from the parking area off Aloe Road, into the lift foyer and offices. | Reserved paraplegic parking should be installed as above. |
| There was an end door, but 6 steps prevented access from Guinea Fowl Road | A 1:12 ramp should be installed to provide access to the road and footpath to the taxi ranks. |
| There were doors at the opposite end of the building that gave level access to parking under Blg 3 and a walkway to Blg 35. | None at present |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the LGF. |
| GROUND FLOOR |  |
| The access from the residences was thru Blg 35 up ramp R35A, 1:12, up ramp R10A, 1:10, up R10, 1:15, to the GF foyer. The access from Blg 9 and Blg 1 was up ramp R10, 1:15, to the GF foyer. | None |
| There was a payphone PP10 in the foyer but the top control was too high at1600. | The phone should be lowered to below 1200. |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the GF. |
| FIRST FLOOR |  |
| There was level access through a passage from Blg 5. | None |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the FF. |

HUMAN MOVEMENT SCIENCE 	AND BIOKINETICS : BLG 11

Two-story building without a  lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were two paraplegic parking signs at the brick paving at the rear of the building, but no demarcation of bays. There was also parallel parking on Kiewet Road, 500m away down a slope. | Parking for disabled people should be relocated in front of the main door (not the door at the bottom of the ramp down to Biokinetics). Three 3500 paraplegic bays should be installed and the route to the entrance should be under cover. This will provide reserved parking for Blg 11 and Blg 6. There would also be level access into the Biokinetics section. |
| GROUND FLOOR |  |
| There was level access to the main entrance and GF foyer from the side road off Kiewet Road, and via a covered walkway from Blg 6 LGF. | None. |
| The two very narrow 2x500 doors into the reception area, offices and toilets were not accessible unless both were open. | The double doors should be replaced by a 900 door with hinged side panel. |
| The M toilet was totally inaccessible down 9 steps, then up 9 steps. The F toilet was also not accessible - standard WC cubicle step-up shower, no space or fittings. | A unisex paraplegic toilet should be installed on the GF with roll-in shower and changeroom facilities. |
| FIRST FLOOR |  |
| The was no access to the FF rooms except via stairs which had a dangerous open riser design. | A list should be installed. The risers of the stairs should be closed in for the safety of people who use crutches or walking sticks. |
| There were no toilets on the FF. | A unisex paraplegic toilet should be installed on the FF. |
| BIOKINETICS CENTRE | (A ground floor section of Blg 11) |
| The side entrance nearest the parking area at the back of the building was down a 1:10 ramp to a door with a bell push to summon assistance if required to get into the lower foyer and then up a 1:7 steep slope up to the biokinetics exercise level. The slope had slippery glazed tiles and no handrails. | This entrance should not be used by disabled people. They should use the main entrance further along the building. Note the recommendations above for relocating the paraplegic parking. |
| The M toilets were up several steps and not accessible - standard WC cubicles with no space or fittings, and step-up showers. The F toilets were at GF level but not accessible – standard WC cubicles with no space or fittings, and step-up showers. Off the side entrance lower foyer there was a unisex semi-paraplegic toilet (non-standard layout and grab rails) and roll-in shower. Unfortunately the location was not accessible due to the steep ramp. | A unisex paraplegic toilet and roll-in shower should be installed on the GF. |

BIOLOGICAL SCIENCES: BLG 12

A five-story H-shaped building with one passenger and one goods lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There was no reserved parking near the building. The nearest parking area was off Protea/Duiker Road. From the parking area there was a very long uncovered path (about 100m) to the LGF side entrance. | Paraplegic bays should be installed close to the LGF side entrance. The reserved bays and the route to the entrance should be under cover. |
| There were herring-bone parking bays along the dimly lit one-way Kieviet Tunnel Rd. The route to Blg 12 was then up Gecko Road, R12, 1:12, 25m long, to loading bays, up a short 1:6 ramp R12A, to the LGF main entrance. | Reserved parking on Kievet Road is not recommended ( too dangerous, too far). Paraplegic parking bays should be installed close to the front of the LGF . These would also serve the GF of Blg 87. |
| A lift served the five floors. It did not meet the paraplegic spec in several respects, (space not deep enough, top buttons too high, no Braille, but could be used by a wheelchair user. There was also a second identical lift reserved for goods only. | In view of the size of the building, both lifts should be made available for passengers. The depth should be increased from 1200 to 1400 min, top buttons lowered from 1400 to 1200. Braille notation and audio annunciators should be fitted. |
| The double doors at each end of the foyer on each floor had large door-stops built into the floor. They were a tripping hazard when only one of the doors is open, particularly for people who are blind or partially sighted. | These hazards should be protected by handrails. |
| Some labs had 2x630 narrow double doors which were not accessible unless both doors were open. | The double doors should be replaced by a 900 door with hinged side panel, or by automatic sliding doors. |
| There were M and F toilets mid-way between floors, accessed only by stairs from floors above or below and therefore totally inaccessible. | A unisex paraplegic toilet should be installed on each floor. |
| LOWER GROUND FLOOR |  |
| Mainly a storage and workshop area, with wide corridors to roller doors for vehicle access from Mongoose Road. | None. |
| The M toilet was not accessible - standard WC cubicles with no space or fittings. There was a step-up shower. | A unisex paraplegic toilet should be installed on the LGF. |
| ZOOLOGY DEPT ON LGF |  |
| The M toilet was not accessible - standard WC cubicles with no space or fittings. There was a step-up shower. | None – see below. |
| The Change Room was not accessible - there was a 580 width restriction preventing access to standard WC cubicles with no space or fittings, and a step-up shower. | A unisex paraplegic toilet and roll-in shower should be installed |
| The doorway to the First Aid Room was congested and the bed too high (750) for wheelchair users. | This facility should be reviewed by the Health Centre |
| GROUND FLOOR |  |
| There was pedestrian access from Blg 6 or the Blg 8 Library forecourt, up a 1:12 ramp, turn R past Blg 87, to the GF entrance. | None |
| The labs and offices were generally accessible. | Specific workstations may require modification for knee room and reach height. |
| There were no accessible toilets on the GF. | A unisex paraplegic toilet should be installed on the GF. |
| FIRST FLOOR |  |
| The labs and offices were generally accessible. | Specific workstations may require modification for knee room and reach height. |
| There were no accessible toilets on the GF. | A unisex paraplegic toilet should be installed on the GF. |
| SECOND FLOOR |  |
| The labs and offices were generally accessible. | Specific workstations may require modification for knee room and reach height. |
| There were no accessible toilets on the GF. | A unisex paraplegic toilet should be installed on the GF. |
| THIRD FLOOR |  |
| The labs and offices were generally accessible. | Specific workstations may require modification for knee room and reach height. |
| There were no accessible toilets on the 3F. | A unisex paraplegic toilet should be installed on the 3F. |

PHYSICS AND CHEMISTRY: BLG 13

A five-story H-shaped building with one passenger and one goods lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There was no parking near the building. The nearest parking area was outside the LGF of Blg 7, unreasonably far from Blg 13. | A side road should be made off Kiewet or Bushbuck Road to the LGF side entrance. Three 3500 paraplegic bays should be installed close to the entrance. The reserved bays and the route to the entrance should be under cover. |
| There were herring-bone parking bays along the dimly lit one-way Kieviet Tunnel Rd. The route to Blg 13 was then up the 1:12 slope of Hoepoe Road, 25m long, to loading bays, then up a short 1:6 ramp to the LGF main entrance. | Reserved parking on Kievet Road is not recommended ( too dangerous, too far). Paraplegic parking bays should be installed close to the front of the LGF . These would also serve the GF of Blg 86. |
| A lift served the five floors. It did not meet the paraplegic spec in several respects, (space not deep enough, top buttons too high, no Braille, but could be used by a wheelchair user. There was also a second identical lift reserved for goods only. | In view of the size of the building, both lifts should be made available for passengers. The depth should be increased from 1200 to 1400 min, top buttons lowered from 1400 to 1200. Braille notation and audio annunciators should be fitted. |
| The double doors at each end of the foyer on each floor had large door-stops built into the floor. They are a tripping hazard when only one of the doors is open, particularly for people who are blind or partially sighted. | These hazards should be protected by handrails. |
| Some labs had 2x630 narrow double doors which were not accessible unless both doors were open. | The double doors should be replaced by a 900 door with hinged side panel, or by automatic sliding doors. |
| There were M and F toilets mid-way between floors, accessed only by stairs from floors above or below and therefore totally inaccessible. | A unisex paraplegic toilet should be installed on each floor. |
| LOWER GROUND FLOOR |  |
| Mainly a storage and workshop area, with wide corridors to roller doors for vehicle access from Bushbuck Road. | None. |
| There was a M toilet which was the only one accessible to a disabled people, providing the lift was working. Some paraplegic facilities had been installed. | A unisex paraplegic toilet should be installed on the LGF. |
| A new Computer Learning Centre was to be built in the area of present mechanical w/shop. | This will further justify the recommendations for paraplegic facilities. |
| GROUND FLOOR |  |
| There was pedestrian access from Blg 7 or the Blg 8 Library forecourt, up a 1:12 ramp, turn R past Blg 86, to the GF entrance. | None |
| The labs and offices were generally accessible. | Specific workstations may require modification for knee room and reach height. |
| There were no accessible toilets on the GF. | A unisex paraplegic toilet should be installed on the GF. |
| FIRST FLOOR |  |
| The labs and offices were generally accessible. | Specific workstations may require modification for knee room and reach height. |
| There were no accessible toilets on the FF. | A unisex paraplegic toilet should be installed on the FF. |
| SECOND FLOOR |  |
| The labs and offices were generally accessible. | Specific workstations may require modification for knee room and reach height. |
| There were no accessible toilets on the 2F. | A unisex paraplegic toilet should be installed on the 2F. |
| THIRD FLOOR |  |
| The labs and offices were generally accessible. | Specific workstations may require modification for knee room and reach height. |
| There were no accessible toilets on the 3F. | A unisex paraplegic toilet should be installed on the 3F. |

THE KRAAL -  STUDENT AND STAFF CAFETERIAS AND BANKING SERVICES: BLG 14

A two-story building without a lift. Users of wheelchairs and other people with mobility problems found the building very difficult to access.

The GF was at the same level as the Kiewet Tunnel Road and therefore below the level of  most of the surrounding buildings.   The FF was at the same level as the LGF of nearby Blgs 6 and 7, but there were no accessible links to those buildings.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| The nearest parking was along Kiewiet Tunnel Road. The parking bays are all reserved for staff working in nearby buildings and none were reserved for disabled people. | 3500 wide paraplegic parking bays should be installed near the level passage to Blg 14. These would give access to the GF sections of the Kraal, and also to the ATM’s and ABSA Branch office. |
| The nearest parking reserved for disabled people was two bays in the parking area off Cross Berry Road, by Blg 7. There was no safe access to the Kraal as the long vehicle ramp from Blg 7 LGF down to Kiewet Tunnel Road was dangerously steep (1:6). | Options should include – * A 1:12 paraplegic ramp should be installed between Blg 7 LGF and the walkway outside Blg 14 FF, and a lift should be installed between the FF and GF of Blg 14. The ramp would also provide access to the CBFM studios. See below. * A series of paraplegic ramps should be installed across the open terraces between Blg 6 and Blg 7 GF, to provide access to Blg 14 GF. |
| There was a walkway at FF level past the CBFM studio and the Student and Staff FF function rooms but it was not accessible because of several steps.. The walkway was less than 1m above the LGF of Blg 7. It should therefore be possible to install a 1:12 ramp parallel to the top of the vehicle ramp up from Kiewet Tunnel Road, to bypass the steps outside the CMFM studios, and make the FF function rooms accessible. | A 1:12 paraplegic ramp should be installed between Blg 7 LGF and the walkway outside Blg 14 FF to provide access to the CBFM Studios and the FF function rooms. NB – Since the assessment, a 1:9 ramp, approx 6m long has been installed to give access from Blg 7, LGF to the FF walkway outside Blg 14.. |
| From Blg 6 LGF, there was a long two-section ramp , top 1:12, 20m long no landing until turn, bottom 1:15, 15m long, no landing until bottom, then level access to Blg 14 GF. These ramps are accessible only for very strong paraplegics and users of electric powered wheelchairs. | Alternative paraplegic ramps should be installed to travel between Blg 6 LGF and Blg 14 GF and FF. |
| BANKING SERVICES – GF LEVEL |  |
| None of the banking facilities were accessible to users of wheelchairs. The ABSA Branch office was not accessible because of a 140 step up to a security passage 680 wide, 820 long and no bypass door. | ABSA should be asked to make their branch accessible. |
| The ABSA , FNB and STANDARD ATM’s were all over 1400 high - too high to be operated when seated in a wheelchair. | The ATM’s should be lowered to an accessible height. (below 1200) |
| All the Telkom payphones were too high (1700) to be operated when seated in a wheelchair. | The payphones should be lowered to an accessible height. (below 1200) |
| There was a toilet block on the GF outside the Students Kraal. The M toilet included an accessible cubicle but there was no sign to indicate this. The F toilet was not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed in this public area. |
| CBFM STUDIOS (Blg 14 FF) |  |
| There was no access to the CBFM Studios except via steps from Blg 7 LGF. | See above for recommendations. NB – Since the assessment, a 1:9 ramp, approx 6m long has been installed to give access from Blg 7, LGF to the FF walkway outside Blg 14.. |
| STUDENTS CAFETERIA |  |
| The 110 step up to the main GF entrance double doors had been ramped at 1:9. There was no landing which made it difficult for a wheelchair user to push one of the doors inwards without assistance.. There was also a second double door entrance with a step which had not been ramped. | Paraplegic ramps should be installed at both entrances. |
| The main counter was not accessible. The approach was restricted by an array of railings 680 apart. The food counter was at 1050 with tray slide at 820. | Spacing between the railings should be increased to 1200. |
| The approach to the snack counter was not obstructed, The counter is at 1000 but there was no tray slide. | A tray slide should be installed 800 high. |
| There were no M or F toilets on the GF. | A unisex paraplegic toilet should be installed on the GF. |
| ##### STUDENTS FUNCTION ROOM |  |
| There was a 100 step up to the double doors, into a hall with loose tables. | A paraplegic ramp should be installed at the entrance. |
| There were no M or F toilets on the GF. | A unisex paraplegic toilet should be installed on the GF. |
| There was an internal staircase up to the balcony. The open riser design is dangerous for a person using a crutch or walking stick. NB. The open area below the stair case results in parts protruding below 2000, which could be a hazard to blind people. | The risers of the staircase should be enclosed. The open area under the staircase should be cordoned-off with eg planters. |
| ##### FIRST FLOOR INTERNAL BALCONY |  |
| There was no access from GF function room below, except up a staircase. | A paraplegic lift should be installed. |
| There was an entrance from the external FF walkway, but the walkway was itself not accessible except up steps at the Blg 7 end. | A 1:12 paraplegic ramp should be installed between Blg 7 LGF and the walkway outside Blg 14 FF to provide access to the FF function rooms. NB – Since the assessment, a 1:9 ramp, approx 6m long has been installed to give access from Blg 7, LGF to the FF walkway outside Blg 14.. |
| There are booths with tables 730 under, with fixed bench seats that are not accessible. | Some loose tables, 750 under, and chairs should be provided. |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the FF. |
| STAFF CAFETERIA |  |
| The 110 step up to the main entrance double doors had been ramped at 1:9. There was no landing, which made it difficult for a wheelchair user to push one of the doors inwards without assistance. | A Paraplegic ramp should be installed at the entrance. |
| The main service counter was 1030 high, with a tray slide at 830. There was a screen wall in front of the counter which limited access. There was no sign to indicate entry and exit. New visitors, which included ourselves for the first couple of visits, appeared somewhat confused. | The passage past the tray slide should be widened to at least 1200. A sign should indicate the direction of flow. |
| The Coffee/Snack Bar was a novel design but had poor accessibility. The wide door-less entrance was obstructed by the coffee service table. The counter was too high at 1200. The door-less exit 860 wide at other end was difficult to negotiate if customers were sitting at bar stools. | There should be a clear passage 1200 wide behind customers sitting at the bar stools. At least 1m of the counter should be lowered to 950 high. |
| At both service areas, the menus were on A4 sheets, mounted on the walls over 2m from the counter and very difficult to read. | The menus should be clearly readable from the counters. Loose copies with large type, and Braille copies should be available at the counter. |
| The main seating area had loose tables and chairs, 700 under, in carpeted areas around a wooden ‘dance floor’. | Some tables should be increased to 750 under. |
| The M and F toilets were not accessible – standard WC cubicles with no space or fittings. | A unisex paraplegic toilet should be installed on the GF. |
| There was an internal staircase up to the balcony. The open riser design wasa dangerous for a person using a crutch or walking stick. NB. The open area below the stair case results in parts protruding below 2000, which could be a hazard to blind people. | The risers of the staircase should be enclosed. The open area under the staircase should be cordoned-off with eg planters. |
| STAFF FUNCTION ROOMS (FF) |  |
| There was no access from the cafeteria below except up a staircase. | A paraplegic lift should be installed. |
| There was an entrance from the external FF walkway, but the walkway was itself not accessible except up steps at the Blg 7 end. | A 1:12 paraplegic ramp should be installed between Blg 7 LGF and the walkway outside Blg 14 FF to provide access to the FF function rooms. NB – Since the assessment, a 1:9 ramp, approx 6m long has been installed to give access from Blg 7, LGF to the FF walkway outside Blg 14.. |
| There were no M and F toilets on the FF. | A unisex paraplegic toilet should be installed on the FF. |

UNIVERSET LECTURE HALLS: BLG 35

A three-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There was a semi- reserved parking space off Aloe Road, outside the LGF back door. The demarcation and signage were not standard and the bay was often abused.. | This bay should be replaced by three 3500 wide paraplegic bays with the correct demarcation and signage, which should be enforced. |
| There were long open paths from the residences over 100m away. These were very arduous for disabled people to travel, especially in hot or wet weather. | The paths should be covered and windbreaks installed. |
| LOWER GROUND FLOOR |  |
| The end entrance next to the reserved parking and G17, had a steep 25 sill bevelled at 1:6. | The sill should be bevelled at 1:10. |
| There was side entrance from the gardens between Blg 35 and Blg 10. The doors were stiff and difficult to open. There was a very short 900 landing outside, difficult to negotiate. There was a steep 1:7 ramp without handrails down to path level. There was then a steep 1:8 ramp, without handrails, up to the garden level. From the lower path, wheelchair users had to use the service path to reach a 1:10 ramp up to the service doors into the bottom level of 350101. The service door was very difficult to negotiate as it opened out onto a narrow 700 landing. | 1:12 paraplegic ramps should be installed to give safe access to the gardens. See below (FF) for comments on access to room 350101. |
| The M and F toilets on the LGF each included a cubicle with some- paraplegic features. | The cubicles in both toilets should be upgraded to the full paraplegic spec. |
| Some of the lecture rooms were flat, others sloped 1:10 down to the front. In some rooms the seats at the end of the back row had been removed, but it was still difficult for a wheelchair user to manoeuvre into position, and then the wheelchair obstructed students wishing to get to other seats in the row, or down the aisle towards the front.. | A minimum space of 1500 diameter should be made at each end of the back row, with a bench 750 under at the front of the space for the use of the wheelchair user.. |
| Inside the building there was a 1:10 ramp, 4m long, between the LGF and GF. There were no handrails. | The ramp should be upgraded to the paraplegic standard, including handrails. |
| GROUND FLOOR |  |
| From Blg 10 there was a 1:12 covered ramp down to the main GF entrance. The ramp was 20 m long, had no hand rails and had no level landings except at each end. | Paraplegic handrails should be installed. A sign should be put up to warn PWD’s that there is a long ramp without landings. |
| There was a side entrance for access from the path from the residences with a 1:12 temporary wooden ramp up from the path level. It had no handrails. Plywood becomes slippery and dangerous when wet. | The temporary ramp should be replaced by a permanent paraplegic ramp. NB: Since the assessment, the wooden ramp has been replaced by brick paving. |
| There were no M and F toilets on the GF. | A unisex paraplegic toilet should be installed on the GF. |
| All the Telkom payphones were too high (1600) to be operated when seated in a wheelchair. | The payphones should be lowered to an accessible height. (below 1200) |
| Some of the lecture rooms were flat, others sloped 1:10 down to the front. In some rooms the seats at the end of the back row had been removed, but it was still difficult for a wheelchair user to manoeuvre into position, and then the wheelchair obstructed students wishing to get to other seats in the row, or down the aisle towards the front.. | A minimum space of 1500 diameter should be made at each end of the back row, with a bench 750 under at the front of the space. |
| FIRST FLOOR |  |
| There was no access to the FF except via stairs. | A paraplegic lift should be installed between the GF and FF. |
| There were no M and F toilets on the GF. | A unisex paraplegic toilet should be installed on the GF. |
| Some of the lecture rooms were flat, others sloped 1:10 down to the front. In some rooms the seats at the end of the back row had been removed, but it was still difficult for a wheelchair user to manoeuvre into position, and then the wheelchair obstructed students wishing to get to other seats in the row, or down the aisle towards the front.. | A minimum space of 1500 diameter should be made at each end of the back row, with a bench 750 under at the front of the space. |
| One of the largest and most frequently used lecture rooms, 350101, was very steep with the entrances on the FF, and a steep slope inside down to the front, and a service door at LGF level. It was very difficult and time consuming for a wheelchair user to access as it was necessary to first exit the LGF of the building at the side door, and then use a series of ramps to get down to the back of the building and enter the lower service door, having checked first that it would be unlocked. | Lecture scheduling should take note of the lack of access to this lecture room. Disabled students should not be expected to attend lectures in 350101 until a lift has been provided to the FF. |

NEW 400 SEAT LECTURE HALL: BLG  ?

#### A single story two-level building

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There was no parking reserved for disabled people near the building. The nearest parking area was the main car park at Blg 9, Embizweni, over 100m away across open paths. | Three 3500 paraplegic bays should be installed close to the main entrance. The reserved bays and the route to the entrance should be under cover. |
| There were fairly level paths to the main entrance from the residences and from the rear exit of Blg 1, Main Building. | Covers and windbreaks should be installed on some of these high traffic routes. |
| There was a steep 1:6 path to the main entrance from the rear entrance of Blg 35. | The path should be modified to a 1:10 paraplegic ramp. |
| The main entrance had a 30 step up between the brick paving outside, and the tiled porch. There was then a further 30 step up between the porch and the foyer inside. This is an example of poor design, or lack of vigilance during the construction of even this newest building. | The tiles in the porch should be taken up and re-laid to provide step-free access between the brick paving and the foyer. |
| The were no toilets in the new building. The nearest toilets were at the other end of Blg 35, on the LGF. | A unisex paraplegic toilet should be installed on the GF near to the lecture hall. |
| There was level access into the lecture hall. There was a level area on both side, about 2500 wide to accommodate wheelchairs. At the front of each level area was an accessible bench, 740 under. The floor then sloped down at 1:12, with 11 rows of articulated seats to the front of the hall. Behind the level areas, there were three tiers of fixed seating. | None – this is an example of satisfactory access for wheelchair users. |

GOLDFIELDS SOUTH, SRC AND SOCIETIES: BLG 86

A two-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There was no parking near the building. Reserved parking on Kievet Road is not recommended ( too dangerous, too far). | Paraplegic parking bays should be installed close to the front of the LGF of Blg 13. These would also serve the GF of Blg 86. |
| From the library forecourt, the main entrance with automatic sliding doors was onto a landing but there was no further access except via stairs up to the FF and down to the GF. | A paraplegic lift should be installed between the GF and FF. |
| GROUND FLOOR | (SRC offices and conference room) |
| There was only dangerous access from Gecko Road because of a steep ramp up to the door to GF. | A 1:12 paraplegic ramp should be installed off Gecko Road to give access to the GF. |
| The toilets were not accessible. One of the wide cubicles in each of the M and F toilets had been equipped with non-standard handrails, but because the WC pan was mounted centrally, there was not enough space for a wheelchair user to enter and transfer. There was no handbasin in the cubicle. These were typical of toilets provided for aged and other frail people who can stand a walk a short distance. | A unisex paraplegic toilet should be installed on the GF. |
| There was a steep ramp without handrails into the conference room. | A 1:10 paraplegic ramp should be installed. |
| FIRST FLOOR | (Student Societies) |
| The side door from the paved way in front of Blg 13 GF was usually locked , but gave level access to the FF only. | A call button should be installed outside this door to call for assistance to enter. |
| There were no toilets on the FF. | A unisex paraplegic toilet should be installed on the FF. |

GOLDFIELDS NORTH, OPPIDANI CENTRE, CITIWISE DRIVERS CLUB: BLG 87

A two-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There was no parking near the building. Reserved parking on Kievet Road is not recommended ( too dangerous, too far). | Paraplegic parking bays should be installed close to the front of the LGF of Blg 12. . These would also serve the GF of Blg 87. |
| From the library forecourt, the main entrance with automatic sliding doors was onto a landing but there was no further access except via stairs up to the FF and down to the GF. | A paraplegic lift should be installed between the GF and FF. |
| GROUND FLOOR | (Oppidani Centre and games area) |
| The only access from Gecko Road was dangerous because of three steep ramps up to the door to GF. | A 1:12 paraplegic ramp should be installed off Gecko Road to give access to the GF. |
| The toilets were not accessible. One of the wide cubicles in each of the M and F toilets had been equipped with non-standard handrails, but because the WC pan was mounted centrally, there was not enough space for a wheelchair user to enter and transfer. There was no handbasin in the cubicle. These were typical of toilets provided for aged and other frail people who can stand a walk a short distance. | A unisex paraplegic toilet should be installed on the GF. |
| FIRST FLOOR | (Citiwise Drivers Club) |
| The side door from the paved way in front of Blg 12 GF was usually locked , but gave level access to the FF only. | A call button should be installed outside this door to call for assistance to enter. |
| There were no toilets on the FF. | A unisex paraplegic toilet should be installed on the FF. |
| Citiwise had no cars with hand controls but had some experience with teaching paraplegic drivers who had their own cars. | ?? |

APPENDIX C : ASSESSMENT OF THE ON-CAMPUS RESIDENCES

The UPE On-campus Residences included the main residence buildings Veritas, Unitas, Melodi, and Xanadu, their annexes, and the two swimming pools and club houses.

The residences were assessed to determine any barriers that would prevent a disabled person from freely accessing the  buildings and facilities to reside or work there, including disabled students, disabled employees, disabled suppliers, and  other disabled visitors.

SUMMARY

At the time, Melodi Annexe was home to two paraplegic wheelchair users  who were able to put up with relatively primitive facilities as they had good arm function.

Only the Ground Floor of each residence block was accessible as there were no lifts to the upper three floors. It has been assumed that to increase the number of flats for disabled students, the ground floor flats would be upgraded first, before installing lifts to the upper floors.

There were no emergency evacuation procedures on display.

There was no covered walkway between Veritas/Unitas and Melodi/Xanadu, which is a particular problem for slow moving disabled students during bad weather.

Parking bays– there were none reserved for disabled people.

Ramps – most buildings and facilities had steps,  or ramps that were too steep.

Outer doors – Either had metal security gates, or were locked.

Double Doors in corridors – not accessible when one side was bolted at the top.

Door closers should be set to delayed action, and minimum closing pressure.

Toilets – there were no fully accessible paraplegic toilets, showers or bathrooms.

Lifts – the multi-story buildings did not have lifts

Swimming pools – there were no ramps to assist disabled  people to  get into the pools.

Pay phones – all were too high to be operable when seated in a wheelchair.

Part of upgrading the facilities should be the installation of the correct signs to guide disabled people to  accessible facilities.

The shuttle service was not accessible for wheelchair users as the vehicles had no space or hoists.

There was an arrangement with Hurter’s Cabs to transport disabled students to doctor etc

at UPE cost, but this was only accessible for disabled students who could transfer independently from wheelchair chair into the taxi.

It was noted that in future, post- merger, there would be more movement between campuses.

### VERITAS RESIDENCE -  FOR FEMALE STUDENTS

A four-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were no emergency evacuation procedures on display. There could be a particular danger to occupants who are sleeping or have mobility problems. | Evacuation procedures should be displayed at 1200 high, in print and Braille. Evacuation drills should be practised and include disabled students and staff. There should be visual and audible alarms. |
| There were many open and covered parking bays in near the buildings but none had been reserved for disabled people. | One reserved 3500 wide bay to the paraplegic spec should be installed near the entrance to the building. |
| There was no safe access onto the pavement. A 1:6 ramp had been installed to the 160 curb, jutting out into the roadway, but it was too steep and narrow for independent use. | The steep ramp should be removed and replaced by sloping a section of the pavement at 1:10 down to road level and to the para spec. |
| The paths and paving up to the front entrance were very uneven and difficult to traverse when using a wheelchair or other mobility aid. | All paving in the area should be checked and maintained smooth. Some wheelchair users feel considerable pain when on bumpy ground. |
| The main entrance had a security tag reader at 1300 and intercom at 1500, both of which were difficult to reach when seated in a wheelchair.. | Both devices should be lowered to 1200 |
| There was no covered walkway between Veritas/Unitas and Melodi/Xanadu, which is a particular problem for slow moving disabled students during bad weather. | Covered walkways should be installed at strategic places to give optimum access to the dining, study and other communal facilities.. |
| The staff/visitors toilets on the Ground Floor had standard cubicles and were not accessible. There was not enough space for paraplegic facilities. | A unisex paraplegic toilet should be installed for use by disabled students, staff and visitors. |
| Some double doors were not accessible when one side was bolted at the top, out of reach for wheelchair users. | Double doors should be replaced by one 900 with a 500 hinged side panel. |
| The computerised meal booking system was not accessible as the top control was too high at 1500. | The console should be lowered so that the highest operable control is <1200. |
| The payphones at 1600 were too high for a wheelchair user. | The payphones should be lowered so that the highest operable control is <1200. |
| The TV lounge was not accessible as it was sunken 300 below passage level. | A 1:10 paraplegic ramp should be installed. |
| The student’s flats were accessible per se, but not suitable for disabled students. The communal WC was too small, the shower had a 120 step-up and the bath was sunken too low. None were fitted with the minimum paraplegic facilities. | Part of the communal ablutions should be upgraded to the paraplegic spec for the more mobile disabled students. Flats for paraplegic students who cannot walk should have en-suite facilities to be able to dry and dress on the bed, and deal with any incontinence problems in private. A WC and roll-in shower requires a minimum of only 1800 x 1800. A WC, roll-in shower and bath would require a minimum of 3250 x 2250. |
| The First, Second and Third floors were not accessible as there was no lift. | None at present. |
| ### VERITAS ANNEXE – 4 stories without a lift. |  |
| The main entrance was not accessible because there was a 250 step up the curb onto the porch. | A 1:10 ramp should be installed to the para spec |
| Most of the comments on the Veritas main residence apply to the annexe. | See above. |

### THE STUDY CENTRE

A single-story building between Veritas and Unitas.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There was level access from the paving outside Unitas, and via a level passage from Veritas. There was also a 1: x ramp into the passage from the gardens. | All paving in the area should be checked and maintained smooth. Some wheelchair users feel considerable pain when traversing bumpy ground. |
| The M and F toilets had standard WC’s and were not accessible. Paraplegics had to go back to their flats. | A unisex paraplegic toilet should be installed for use by disabled students, staff and visitors. |
| The tables (690 under) in the study room and computer centre had no knee room for wheelchair users. | Some of the tables in the study room and computer centre should be raised to 750 under. |

### EX - GUEST BLOCK, now converted to a  Student Residence

A three-story building without a lift, adjacent to the Study Centre.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were several parking bays at the end of the building but none had been reserved for disabled people. | One reserved 3500 wide bay to the paraplegic spec should be installed near the entrance to the building. |
| There was no access onto the 150 pavement. | A curb cut should be installed, ramped at 1:10 to the para spec. |
| The paths and paving up in the area were very uneven and difficult to traverse when using a wheelchair or other mobility aid. | All paving in the area should be checked and maintained smooth. Some wheelchair users feel considerable pain when traversing bumpy ground. |
| There was level access into the Ground Floor where there was only a laundry. The flats on the First and Second Floors were not accessible as there was no lift. | None at present. |

### UNITAS RESIDENCE -  FOR MALE STUDENTS

A four-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were no emergency evacuation procedures on display. There could be a particular danger to occupants who are sleeping or have mobility problems. | Evacuation procedures should be displayed at 1200 high, in print and Braille. Evacuation drills should be practised and include disabled students and staff. There should be visual and audible alarms. |
| The main parking area was off ?? Road, some way from Unitas. | Curb cuts to the para spec should be installed to give smooth access onto the pavements. Interconnecting pathways should be checked and maintained smooth. Some wheelchair users feel considerable pain when traversing bumpy ground. |
| There were a few parking bays in front of the main entrance but none had been reserved for disabled people. | One reserved 3500 wide bay to the paraplegic spec should be installed near the entrance to the building. |
| The porch at the main entrance was 150 above road level. It had been made accessible by a 1:8 ramp, which was steeper than the para spec, and had no curbs or handrails. | The ramp should be rebuilt at 1:10 to the para spec. |
| The main entrance had a security tag reader at 1300 and intercom at 1500, both of which were difficult to reach when seated in a wheelchair.. | Both devices should be lowered to 1200 |
| The staff/visitors toilets on the Ground Floor had standard cubicles and were not accessible. There was not enough space for paraplegic facilities. | A unisex paraplegic toilet should be installed for use by disabled students, staff and visitors. |
| Some double doors were not accessible when one side was bolted at the top, out of reach for wheelchair users. | Double doors should be replaced by one 900 with a 500 hinged side panel. |
| The computerised meal booking system was not accessible as the top control was too high at 1500. | The console should be lowered so that the highest operable control is <1200. |
| The payphones at 1600 were too high for a wheelchair user. | The payphones should be lowered so that the highest operable control is <1200. |
| Fire extinguishers in the passages were at a dangerous height for wheelchair users and blind and partially sighted people. | Such protruding objects should be repositioned so that they are not a safety hazard. |
| The SuperTuck Shop off the pool room was accessible but the corner of shelf just inside the door jutted out at wheelchair head height. | Such protruding objects should be modified or repositioned so that they are not a safety hazard. |
| The student’s flats were accessible per se, but not suitable for disabled students. The communal WC was too small, the shower had a 120 step-up and the bath was sunken too low. None were fitted with the minimum paraplegic facilities. Metal seats in the showers are dangerous and could lead to pressure sores. | Part of the communal ablutions should be upgraded to the paraplegic spec for the more mobile disabled students. Flats for paraplegic students who cannot walk should have en-suite facilities to be able to dry and dress on the bed, and deal with any incontinence problems in private. A WC and roll-in shower requires a minimum of only 1800 x 1800. A WC, roll-in shower and bath would require a minimum of 3250 x 2250. |
| The First, Second and Third floors were not accessible as there was no lift. | None at present. |
| ### UNITAS ANNEXE – 4 stories without a lift. |  |
| There was a large open parking area near the main entrance but none of the bays had been reserved for disabled people. | One reserved 3500 wide bay to the paraplegic spec should be installed near the entrance to the building. |
| There were two curb cuts near the building, but the surfaces were not step-free. | Both curb cuts and the nearby paths to the building and to the pathway to the main campus should be refurbished to smooth surfaces. The road surface in front of the curb cuts should be demarcated to prevent vehicles from blocking access. |
| From the main entrance there were 6 x 150 steps down to the pathway to Unitas main residence. | A 1:12 ramp should be installed to the para spec, to provide access between the two buildings and hence to the study centre etc. |
| Most of the comments on the Unitas main residence apply to the annexe. | See above. |

### MELODI RESIDENCE -  FOR FEMALE STUDENTS

A four-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were no emergency evacuation procedures on display. There could be a particular danger to occupants who are sleeping or have mobility problems. | Evacuation procedures should be displayed at 1200 high, in print and Braille. Evacuation drills should be practised and include disabled students and staff. There should be visual and audible alarms. |
| There were many open and covered parking bays off Aloe Road, in near the buildings but none had been reserved for disabled people. | One reserved 3500 wide bay to the paraplegic spec should be installed near the entrance to the building. |
| The porch at the main entrance was 250 above road level but part of the steps had been bypassed and made accessible by a 1:10 ramp, with walls that served as rails and curbs. | None. |
| The main entrance had a security tag reader at 1300 and intercom at 1500, both of which were difficult to reach when seated in a wheelchair.. | Both devices should be lowered to 1200 |
| There was no covered walkway between Veritas/Unitas and Melodi/Xanadu, which is a particular problem for slow moving disabled students during bad weather. | Covered walkways should be installed at strategic places to give optimum access to the dining, study and other communal facilities.. |
| The staff/visitors toilets on the Ground Floor had standard cubicles and were not accessible. There was not enough space for paraplegic facilities. | A unisex paraplegic toilet should be installed for use by disabled students, staff and visitors. |
| Some double doors were not accessible when one side was bolted at the top, out of reach for wheelchair users. | Double doors should be replaced by one 900 with a 500 hinged side panel. |
| The computerised meal booking system was not accessible as the top control was too high at 1500. | The console should be lowered so that the highest operable control is <1200. |
| The payphones at 1600 were too high for a wheelchair user. | The payphones should be lowered so that the highest operable control is <1200. |
| The TV lounge was not accessible as it was sunken 300 below passage level. | A 1:10 paraplegic ramp should be installed. |
| The student’s flats were accessible per se, but not suitable for disabled students. The communal WC was too small, the shower had a 120 step-up and the bath was sunken too low. None were fitted with the minimum paraplegic facilities. Metal seats in the showers are dangerous and could lead to pressure sores. | Part of the communal ablutions should be upgraded to the paraplegic spec for the more mobile disabled students. Flats for paraplegic students who cannot walk should have en-suite facilities to be able to dry and dress on the bed, and deal with any incontinence problems in private. A WC and roll-in shower requires a minimum of only 1800 x 1800. A WC, roll-in shower and bath would require a minimum of 3250 x 2250. |
| The First, Second and Third floors were not accessible as there was no lift. | None at present. |
| MELODI ANNEXE – 4 stories without a lift. |  |
| At the time, Melodi Annexe was home to two paraplegic wheelchair users who were able to put up with relatively primitive facilities as they had good arm function. |  |
| There were many open and covered parking bays off Aloe Road, near the buildings but none had been reserved for disabled people. | One reserved 3500 wide bay to the paraplegic spec should be installed near the entrance to the building. |
| The main entrance was not accessible because there was a 250 step up the curb onto the porch. This meant a long detour for the paraplegic wheelchair users to the Melodi main building entrances. | A 1:10 ramp should be installed to the para spec |
| The main entrance had a security tag reader at 1300 and intercom at 1500, both of which were difficult to reach when seated in a wheelchair.. | Both devices should be lowered to 1200 |
| Opposite the main entrance, a side entrance gave level access across to Veritas Annexe, and serious steps down to the gardens. | Ramps to the para specs should be instelled to give access to the gardens. |
| The student’s flats were accessible per se, but not suitable for disabled students. The communal WC was too small, the shower had a 120 step-up and the bath was sunken too low. None were fitted with the minimum paraplegic facilities. The metal seat in the shower was dangerous and could lead to pressure sores. | Flats for paraplegic students who cannot walk should have beds that are easy to move and make-up. Book shelves and clothes rails should be at 1200. There should be en-suite facilities to be able to dry and dress on the bed, and deal with any incontinence problems in private. A WC and roll-in shower requires a minimum of only 1800 x 1800. A WC, roll-in shower and bath would require a minimum of 3250 x 2250. |

### THE DINING HALL

A single-story building between Melodi and Xanadu.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There was no access from the parking bays outside Melodi because of a 150 curb. | A curb cut should be installed to the para spec, to give access to the path alongside the Dining Hall. |
| At the Xanadu end of the Dining Hall, a 1:4 ramp, dangerously steep for wheelchair users had been installed protruding into the road, onto the path by the spiral emergency stairs, for access to the staff quarters and offices, and Dining Hall. | The ramp should be removed and replaced by curb cuts to the para spec. The paving in that area should be modified to give access from the road and parking area outside Xanadu onto the pathway. |
| There was level access into the Dining Hall via passages from Melodi and Xanadu. | None. |
| The one-way entrance passages to the service counters were only 800 and 900 wide and difficult for wheelchair users to negotiate. | The passages should be increased to 1100 wide. |
| The computerised meal ordering system was too high to be used when seated in a wheelchair. | The console should be lowered so that the highest operable control is 1200. |
| The tables did not have knee room for wheelchair users. | Some of the tables should be raised to 750 under. |
| The one-way revolving exit door was too small for wheelchair users, who had to return to the entrance and try to get out against the flow of incoming students. | A side door should be installed for wheelchair users to exit the Dining Room. This could have a security lock accessible only to disabled students. |

### XANADU RESIDENCE -  FOR MALE STUDENTS

A four-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were no emergency evacuation procedures on display. There could be a particular danger to occupants who are sleeping or have mobility problems. | Evacuation procedures should be displayed at 1200 high, in print and Braille. Evacuation drills should be practised and include disabled students and staff. There should be visual and audible alarms. |
| There were many open and covered parking bays near the buildings but none had been reserved for disabled people. | One reserved 3500 wide bay to the paraplegic spec should be installed near the entrance to the building. |
| The porch at the main entrance was 200 above road level but part of the steps had been bypassed and made accessible by a 1:10 ramp, with walls that served as rails and curbs. | None. |
| The main entrance had a security tag reader at 1300 and intercom at 1500, both of which were difficult to reach when seated in a wheelchair.. | Both devices should be lowered to 1200 |
| The staff/visitors toilets on the Ground Floor had standard cubicles and were not accessible. There was not enough space for paraplegic facilities. | A unisex paraplegic toilet should be installed for use by disabled students, staff and visitors. |
| Some double doors were not accessible when one side was bolted at the top, out of reach for wheelchair users. | Double doors should be replaced by one 900 with a 500 hinged side panel. |
| The computerised meal booking system was not accessible as the top control was too high at 1500. | The console should be lowered so that the highest operable control is <1200. |
| The payphones at 1600 were too high for a wheelchair user. | The payphones should be lowered so that the highest operable control is <1200. |
| The student’s flats were accessible per se, but not suitable for disabled students. The communal WC was too small, the shower had a 120 step-up and the bath was sunken too low. None were fitted with the minimum paraplegic facilities. | Part of the communal ablutions should be upgraded to the paraplegic spec for the more mobile disabled students. Flats for paraplegic students who cannot walk should have en-suite facilities to be able to dry and dress on the bed, and deal with any incontinence problems in private. A WC and roll-in shower requires a minimum of only 1800 x 1800. A WC, roll-in shower and bath would require a minimum of 3250 x 2250. |
| The First, Second and Third floors were not accessible as there was no lift. | None at present. |
| XANADU ANNEXE – 4 stories without a lift. |  |
| There were many open and covered parking bays off Aloe Road, across from the building but none had been reserved for disabled people. | One reserved 3500 wide bay to the paraplegic spec should be installed as close as possible to the entrance to the building. |
| There was a 150 step up from the parking area onto the pathway to the building which was about 40 m away. | A curb cut should be installed to the para spec. Interconnecting pathways should be checked and maintained smooth. Some wheelchair users feel considerable pain when traversing bumpy ground. |
| The main entrance had a security tag reader at 1300 and intercom at 1500, both of which were difficult to reach when seated in a wheelchair.. | Both devices should be lowered to 1200 |
| Opposite the main entrance, a side entrance gave access to a limited paved area, then steps 650 down to paths across to the gardens and Unitas Annexe. | 1:12 ramps to the para specs should be installed to give access to the gardens and Unitas. |
| Most of the comments on the Xanadu main residence apply to the annexe. | See above. |

### POOL / CLUB HOUSE  for XANADU and MELODI

A single-story building with an outdoor pool.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| The ramp and path from Aloe Road were very rough and not accessible for wheelchair users. | A 1:10 para ramp should be installed with a smooth path up to the building. |
| The clubhouse was not accessible because of a 150 step up from the patio. | A 1:10 para ramp should be installed into the building. |
| The M and F toilets had standard WC’s and were not accessible. | A unisex para toilet should be installed. |
| There were no change room facilities for wheelchair users. | The above unisex toilet should be made large enough to include a 500 high bench for wheelchair users to transfer onto for drying and dressing after swimming. |
| The pool was not accessible as there was no facility to assist disabled people to get into and out of the pools. | Ramps and handrails should be installed in the pools. In the longer term, a hydraulically operated hoist should be installed. (See note at end of Unitas/Veritas facility below). |

### POOL / CLUB HOUSE for UNITAS and  VERITAS

A single-story building with an outdoor pool.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There was no access for wheelchair users from ?? Road. There was no ramp to get up the 150 curb. There was 30 m of grass to cross before reaching the paved path to the entrance of the pool area. | A 1:10 curb cut to the para spec should be installed at the roadside, with a smooth path up to the entrance. |
| The entrance was not accessible because of a turnstile. There was a swing gate that was open at the time, but the concrete in front of the gate was too rough for access. | The path should be made step-free through the gate. The gate should be left open. |
| The clubhouse was not accessible because of two steps 250 step up from the patio to the large slding doors. | A 1:10 para ramp should be installed into the building. |
| The M and F toilets had standard WC’s and were not accessible. | A unisex para toilet should be installed. |
| There were no change room facilities for wheelchair users. | The above unisex toilet should be made large enough to include a 500 high bench for wheelchair users to transfer onto for drying and dressing after swimming. |
| The Disco Station in the RH corner was not accessible because of a 180 step up, and a 1500 high counter. | ?? |
| The food service counter at the LH end was not accessible because it was 1200 high and had a 200 x 200 step in front. | A section of the counter at least 1000 long should be lowered to 960 high, and the 200x200 step removed at that point. |
| There were steps into the pool but no facilities to assist disabled people to get into and out of the pool. | Handrails should be installed at the steps. A hydraulically operated hoist should be installed (see below). |
| A second-hand hydraulically-operated hoist to lower disabled people into the pool had been donated to UPE Sport Centre but not yet installed. | If this hoist is not required for the Sport Centre, it should be installed at the clubhouse. |

APPENDIX D : ASSESSMENT OF THE SPORTS FACILITIES

- The UPE sports facilities include the Sport Bureau, Gym and indoor pool,  Indoor sports centre,  Rugby/athletics stadium, Soccer fields and  clubhouse,  Tennis courts and  clubhouse, Cricket fields and clubhouse  and the Campus Boma.

The facilities were assessed to determine any barriers that would prevent a disabled person from freely accessing or working in the building or participating in sports activities, including  disabled athletes, disabled sports officials, disabled spectators, disabled employees, disabled suppliers, and  other disabled visitors.

SUMMARY

The sports facilities were assessed but none met the requirements for accessibility.

There were no emergency evacuation procedures on display.

Parking – there was none reserved for disabled people.

Ramps – most buildings and facilities had steps,  or ramps that were too steep.

Lifts – the two-story buildings did not have lifts

Swimming pool – there were no ramps to assist disabled or aged people to  get into the pool.

Toilets – there were no fully accessible paraplegic toilets.

Change Rooms – none of the change rooms had accessible facilities for paraplegics.

Pay phones – all were too high to be operable when seated in a wheelchair.

Part of upgrading the facilities should be the installation of the correct signs to guide disabled people to  accessible facilities.

### SPORT BUREAU

A two-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were no emergency evacuation procedures on display. | Evacuation procedures should be displayed at 1200 high, in print and Braille. Evacuation drills should be practised and include disabled students and staff. There should be visual and audible alarms. |
| - Street parking along Aloe Road. None had been reserved for disabled people. | - Two bays should be installed for disabled people near to the Main entrance. |
| - Entrance via gentle slope to double sliding doors, 1000 clear opening. Gives good access to the Bureau, Seminar Rooms, Gym and Pool. | - The sliding doors should be automated. |
| - Reception counter too high at 1050[965] | - None at present. |
| - Double security doors controlled by reception. | - None at present. |
| - Offices | - Furniture should be modified as required to accommodate disabled employees. |
| - Toilets – none. The standard toilets in the Indoor Centre are not accessible. The nearest accessible toilets are at the far end of the Indoor centre. | - A unisex accessible toilet should be installed near to Sport Bureau and Gym/Pool. (see below) |
| - There were 20 serious steps on the outside of the building up to the Conference Centre. | - A lift should be installed . |

### GYM AND INDOOR POOL

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| - Level access from Sport Bureau into Gym. - Level access through Gym to Pool. | - Specialised advice should be taken on access to gym equipment as that is beyond the scope this current audit. . Consult DISSA?? |
| - Pool reception counter too high at 1100[965]. | - None at present. |
| - No provision made to assist disabled, elderly and frail people to get into and out of the pools. | - Ramps and handrails should be installed in the pools. |
| - A hydraulically-operated hoist to lower disabled people into the pool has been donated to UPE, but it is not clear why this has not been installed. | - This should be investigated. |
| - The rinse-off shower was not accessible. Too small at 1m x 1m, and 190 step-up entrance. | - To improve safety, the glass screen should be replaced by a solid wall. - The shower should be enlarged to 2m x 1 m and the 190 step should be removed, for disabled people who can walk. - Handrails should be installed at 800. |
| - Toilets and change room. – none. The standard toilets in the Indoor Centre are not accessible, and the change rooms are down serious steps. The nearest accessible toilets are at the far end of the Indoor centre. | - A unisex accessible toilet/shower/ change room should be installed in the Gym/Pool area. This would also provide toilet facilities for disabled people from the Sport Bureau. |

### INDOOR SPORTS CENTRE

A two-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were no emergency evacuation procedures on display. | Evacuation procedures should be displayed at 1200 high, in print and Braille. Evacuation drills should be practised and include disabled students and staff. There should be visual and audible alarms. |
| - Street parking along Protea and Aloe Roads and on grass. No bays have been reserved for disabled people. | See recommendation above for Sport Bureau. Install an additional two bays for disabled people on Protea Road close to the End entrances. |
| Door [1], the main pedestrian entrance next to the Sport Bureau is not accessible due to a 120 step up. | The step should be replaced with a 1:10 ramp. |
| From Protea Road there are short metal ramps onto the 140 pavement. The ramps are buckled. There is a roller door entrance with a 1:8 ramp that is too steep. | The metal ramps and ramp up to the roller door should be replaced by a continuous ramp from road level, maximum gradient 1:10, fanned out to be step-free on all sides. |
| The rear door by the squash courts has a very steep ramp 1:4, too steep to be of any use. The area has low headroom due to the concrete ramps to the first floor | The ramp should be rebuilt to spec. |
| - The two-story building has no lift to the Conference Centre and squash gallery - A rough grass track leads round the Marine Drive side to the back of the sports centre to steep 1:8 and 1:6 ramps up to the first floor. The ramps were poorly sited and too long and steep for independent use. The ramp restricts headroom to the rear door to the squash courts. | A lift should be installed inside the Sports Centre. The steep concrete ramps should only be kept as an emergency exit from the first floor. |
| - Toilets – There are large M and F paraplegic toilets at the Protea Road end. They are not properly laid out or equipped and the shower fittings are incomplete. | Both should be upgraded according to the specs, or preferably install two new unisex toilets. If these are equipped with showers and beds they could also be change rooms. |
| - Change rooms –the main M and F change rooms are down stairs and completely inaccessible. | Two unisex toilet/showers should be installed on the ground floor with beds to change on. (see above) |
| - Terraced seating – not accessible, so wheelchair users and others that cannot climb up to the terrace have to stay at floor level. | Ramps to elevated seating and wheelchair parking should be provided. |
| - Upper seating – not accessible. | Install lift. |
| - Stage – 1300 high with 8x160 steps at each end - not accessible. | A ramp should be installed. |

## RUGBY/ATHLETICS STADIUM

- A two-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| - Street parking along Protea Road. None reserved for disabled people. | - Two parking bays should be reserved for disabled people near to the main spectators entrance, for access to the stadium at track level. |
| - The main pedestrian entrances are 850 clear and accessible. The ticket counter is 1000[965] | - None at present |
| - The M and F toilets at the entrance are not accessible– 80 step up, no paraplegic cubicle. | - A unisex accessible toilet should be provided. |
| - The refreshment counter is at 1000[965] | - None at present |
| - The four payphones were too high at 1600[<1200], and required a long detour around poles and across the grass. | - At least two of the payphones should be re-sited with a smooth apron at ground level, and lowered to 1200. |
| - The terraces are not accessible to wheelchair users. | - Selected areas at track and Clubhouse level should be made accessible and reserved for use by wheelchair users. |
| - Inside the stadium there is a 1: 8 steep ramp 10m long up from track level to 7x160 steps up to the change rooms. The steps have in the past been bridged by a wooden ramp for certain events, but the result is a dangerously steep ramp with a gradient of 1:5. | - Alternative positions should be investigated for an accessible unisex change room. - ? Excavate below the terraces? - ? Build accessible change room by Aloe Road entrance? |
| - The paraplegic toilet in the change room is not correctly equipped or laid out. WC too low at 400[500], rails too high at 1200[900], no hand basin. But the door lock was a good lever design. | - This should be upgrade to spec for athletes that can negotiate the existing ramp and steps. |
| - The three-station shower in the change room was not accessible because of a 130 sill. | - The sill should be removed. - A 900 wide bench, 500 high should be provided for drying and dressing. |
| - RUGBY CLUB HOUSE |  |
| - Access to the Rugby Clubhouse level is via 15x150 steps. There is also a steep 1:8 concrete road up from street level. | - Two parking bays for disabled people should be installed on the concrete slab near the clubhouse. - Disabled people should be allowed to drive in the vehicle entrance and up to the club house. |
| - The end door is not accessible because of steps 2x150 steps. | - A ramp should be built to give smooth access. |
| - The front sliding doors are fairly accessible. | - The apron in front of the sliding doors should be widened to provide a viewing area for wheelchair users. |
| - The M and F toilets in the clubhouse are not accessible. | - A unisex paraplegic toilet should be installed. |
| - The fixed tables in the clubhouse were not accessible, but loose table were available. | - Tables at least 750 under should be provided. |
| - The VIP Lounges and Media Centre were not accessible due to serious steps. | - ? |
| - Wooden chalets | - ? |

### SOCCER CLUBHOUSE

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| - Access via Aloe Road | - None at present |
| - Grass parking by the clubhouse, | - None at present |
| - 100 high steps prevent access to the end and front sliding doors. | - A ramp, max 1:10, should be built to give smooth access. |
| - The M and F toilets in the clubhouse are not accessible. | - A unisex paraplegic toilet should be installed. |
| - The bar counter at 1150[965] is too high | - None at present. |
| - The showers in the M and F change rooms outside are not accessible. There is 100 step up and no paraplegic facilities. | - None at present. If there is a need to upgrade in future, roll-in showers should be provided with a bed on which to dry and dress. |
| - The payphones outside are too high (1600) to reach when seated. | - The phones should be lowered to 1200. |

### TENNIS CLUBHOUSE

| - Access off Ndlovu Road. The approach was via a rough gravel road and was not accessible by wheelchair. | - The track between Ndlovu Road and the clubhouse should be maintained smooth. |
| --- | --- |
| - Grass parking by the clubhouse | - None at present |
| - Only 30 step up to doors | - None at present |
| - The M and F toilets/change rooms are not accessible. | - A unisex paraplegic toilet should be provided with a roll-in shower and a bed on which to dry and dress.. |
| - The bar and snack counters are a little high at 1050[965[ | - None at present |
| - The payphones are too high at 1600[<1200] to reach when seated. | - The phones should be lowered to 1200. |

### CRICKET CLUBHOUSE

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| - Access via Ndlovu Road | - None. |
| - Grass parking by the clubhouse, | - None at present |
| - A 1:9 ramp gave access from grass to porch. | - None at present. |
| - 70 high step prevents access to the sliding doors. | - The step should be bridged by a 1:10 ramp. |
| - The toilets in the clubhouse are not accessible due to 70 and 110 steps. There are no paraplegic facilities. | - A unisex paraplegic toilet should be installed. |
| - The change rooms inside the club house were not accessible due to steps, step-up showers and lack of paraplegic facilities. | - None at present. If there is a need to upgrade in future, accessible toilets and roll-in showers should be provided with a bed on which to dry and dress. |
| - The bar counter and serving hatch are too high at 1150[965]. | - None at present. |
| - There are fixed table and bench units, 750 under. | - None at present. |
| - The payphones are too high at 1600[1200] to reach when seated. | - The phones should be lowered to 1200. |
| - From the porch a steep 1:6 ramp lead down to a narrow 900[1100] wide apron around the building to reach the outside change rooms. | - None at present. |
| - The change rooms outside the club house were not accessible due to high 240 steps, 180 step-up showers and lack of paraplegic facilities. | - None at present. If there is a need to upgrade in future, accessible toilets and roll-in showers should be provided with a bed on which to dry and dress. |

### CAMPUS BOMA

- A large and a small hall, with outside braai facilities.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| - Access via Ndlovu Road | - None. |
| - 20 standard parking bays on tarmac in front of large hall, with grass parking around halls. | - One parking bay should be reserved for disabled people. |
| - 50 step up to porch at front of main hall. | - None at present. |
| - M and F toilets lead off the porch. Level access but no paraplegic facilities. | - A unisex paraplegic toilet should be installed. |
| - The small hall was inaccessible because of 150 step up. | - A ramp, max 1:10, should be built to give smooth access into the hall. |

##### APPENDIX E : ASSESSMENT OF THE BIRD STREET CAMPUS

The UPE Bird Street campus occupies two historic and presumably protected buildings (Eendrag and Wegspring) and  one more modern building (Felstead), all on sloping ground  between Bird Street and Cuyler Street, and another  modern building (SBU) on the other side of Cuyler Street.  There are also several other smaller buildings in the court yard behind Eendrag.

The campus was assessed to determine any barriers that would prevent a disabled person from freely studying,  working  or  visiting the  buildings and other facilities, including disabled students, disabled employees, disabled suppliers, and  other disabled visitors.

SUMMARY

The four buildings were assessed but none met the basic requirements for accessibility.

The only practicable access for wheelchair users was off Cuyler Street into the rear entrances and ground floors of Eendrag and Wegspring, and to SBU.

There were no emergency evacuation procedures on display.

Parking – there was none reserved for disabled people.

Ramps – all the buildings  had serious steps and there were no ramps.

Lifts – the  buildings did not have lifts

Toilets – there were no  accessible paraplegic toilets.

Given the limitations that historic buildings  impose on modifications, it was only possible to provide a few recommendations.

ACCESS FROM BIRD STREET

There were no Reserved parking bays in the public parking  along Bird St. There was a gate for  pedestrians  and authorised vehicles could enter through a card-controlled security boom.

There was a long tarred slope (G=1: 15) with no access to BLG 62, FELSTEAD on the LHS, and   formidable steps (4 steps to grass level, 10 steps to porch) on the RHS up to Blg 61, EENDRAG.

There were 10 standard parking bays on the LHS alongside FELSTEAD, and a parking area with 22 covered bays on the RHS, in front of EENDRAG.

The road  continued up to a flat area with 6 covered parking bays in front of  Blg 65, WEGSPRING, which also had  formidable steps up to the entrance.

The road then continued down past the inaccessible main entrance of FELSTEAD, down to a second card-controlled security boom back onto Bird Street.

General Note - It may be worth looking at how to bridge between these buildings  to give wheelchair access.

NB: Close by, in Annerly Street, at the Lampenhof block of flats was a good example of  an accessible  1:12 ramp, 1300 wide, 14m long,  bridging between the pavement  and the Ground Floor entrance.  Unfortunately, the 1:8 slope leading up from the under-building parking was not accessible.

EENDRAG:  BLG 61

A two-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| Access from Bird Street : See notes above. | - None at present. |
| There were no emergency evacuation procedures on display. | Evacuation procedures should be displayed at 1200 high, in print and Braille. Evacuation drills should be practised and include disabled students and staff. There should be visual and audible alarms. |
| 14 steep steps prevented access to the front entrance. | - None at present: As the parking area in front of the building was down further slopes, it is unlikely that the front entrance could be made accessible for wheelchair users without considerable expense. |
| From Cuyler Street: There was public parking on both sides of the street but no bays reserved for disabled people - Inside the courtyard the ground sloped at 1: 15 down past outbuildings to the rear entrance. Vehicles are allowed into this area to offload wheelchair users as required. | - A 3500 wide bay to the paraplegic spec should be installed in the courtyard close to the rear entrance to the building for use by disabled drivers. |
| - The rear entrance was not easily accessible because of a 90 step up onto the porch, and 2x700 narrow security gates. | - A 1:10 paraplegic ramp should be installed onto the step. The two narrow gates should be replaced by one 900 gate and a 500 hinged panel. |
| - The M and F toilets on the GF were not accessible because of standard cubicles and lack of space for paraplegic facilities. | - A unisex paraplegic toilet should be installed in the building. |
| - From the rear entrance it was not possible for direct access to the admin offices because a stairway down to a cellar restricted the passage to a width of 670. | - A sign and call button should be installed so that paraplegics can access the passage to the admin offices via the security door into the front foyer. - The 80 step up from the foyer to the passage should be bevelled at 1:10. |
| - The spiral staircase in the front foyer was open underneath and a safety hazard at 1500 to 1800 for blind people who may bump their heads. | - A handrail should be installed to prevent people walking into the danger area. |
| - The Reception and Board Room off the front foyer were not accessible because of a 40 step up. | - The steps into the rooms should be bevelled at 1:10. |
| - The lecture rooms off the rear entrance and covered walkway were accessible. | - The height of some tables should be raised to 750 under to give knee space for wheelchair users. |
| - The First Floor lecture rooms and offices were not accessible as there was no lift. | - None at present. |
| - The M student’s toilets across the courtyard had level entrance but the standard cubicles were too small for paraplegic facilities. | - One of the cubicles should be converted for paraplegic use. |
| - The F student’s toilets were not accessible as there were two steps 350 up to the door and the standard cubicles were too small for paraplegic facilities. | - A 1:10 paraplegic ramp should be installed to give access to the F toilets. One of the WC’s should be converted to the paraplegic spec. |
| - The Sick Bay was not accessible as there were two steps 350 up to the door, and there was no en-suite para toilet. - Plans were in hand to relocate the sick bay and convert the space into a unisex paraplegic toilet. | - The new unisex toilet should be to the paraplegic spec. The landing of the new ramp to the F toilets (see above) should be extended to give access to the new unisex toilet. |
| - The Sick Bay was to be relocated to an ex-security office at the end of the covered way from the rear entrance of Eendrag. | - The new sick bay should include an accessible paraplegic toilet. Sick persons often have nausea or gastric problems and require a toilet, one way or the other. Disabled persons may need assistance to deal with incontinence problems. |
| - Also in the courtyard steps prevented access to Lecture Rooms 10 to 13 and the Dining Room . | - 1:10 paraplegic ramps should be installed to these rooms. |

FELSTEAD: BLG 62

A three-story building without a lift, mainly rented out  to tenants.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| - The front entrance was not accessible as there were 15 steps up from Bird Street. | - None at present. |
| There were no emergency evacuation procedures on display. | Evacuation procedures should be displayed at 1200 high, in print and Braille. Evacuation drills should be practised and include disabled students and staff. There should be visual and audible alarms. |
| - In addition to the up-hill road off Bird Street, through a security boom, to the RHS of the building there was another road on the LHS of the building that sloped up to the Main Entrance, past 8 standard parking bays. The road continued to a small parking area at the back of the building which was about 2m above the level of the Main Entrance. . | - None at present. The installation of a rather long 1:12 ramp from the small parking area could be considered if wheelchair access to the building is a requirement. |
| - Another relatively flat entrance at the back only gave access to a landing half way up the internal stairs between the ground and first floors. | - None at present. |
| - The M and F toilets on the GF were not accessible because of standard cubicles and lack of space for paraplegic facilities. | - A unisex paraplegic toilet should be installed for disabled people who can negotiate the steps. |
| - The offices on the GF were accessible once inside the building. | - None at present |
| - The first, second and third floor offices were not accessible as there was no lift. Each floor had the same M and F toilets as on the GF. | - None at present. |

WEGSPRING: BLG 65

A two-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| - The front entrance was not accessible as there were 10 steps up from the small parking area. | - None at present. It could be possible to install a long 1:12 paraplegic ramp across the front of the building. |
| There were no emergency evacuation procedures on display. | Evacuation procedures should be displayed at 1200 high, in print and Braille. Evacuation drills should be practised and include disabled students and staff. There should be visual and audible alarms. |
| - There is a possible accessible route to the rear door of the building via a motorised roller door onto Cuyler Street. | - The logistics and security implications of this route should be investigated. |
| - The M and F toilets on the GF were not accessible because of standard cubicles and lack of space for paraplegic facilities. | - A unisex paraplegic toilet should be installed for disabled people who can negotiate the steps.. |
| - There was level access to the ABSA computer lab and other lecture rooms on the GF | - None at present. |
| - The first floor was not accessible as there was no lift. | - None at present. |

SBU: BLG 57

A two-story building without a lift.

| OBSERVATIONS | RECOMMENDATIONS |
| --- | --- |
| There were no emergency evacuation procedures on display. | Evacuation procedures should be displayed at 1200 high, in print and Braille. Evacuation drills should be practised and include disabled students and staff. There should be visual and audible alarms. |
| The building was surrounded by a flat paved area with about 150 parking bays. | - Two 3500 wide bays to the paraplegic spec should be installed near the entrance to the building. |
| - There were 3 steps 450 up that prevented access to the SBU front entrance. | - A 1:10 ramp to the paraplegic spec should be installed to bypass the steps to the front porch. |
| - The 2x750 front security gates were difficult to negotiate and there was a 60 step up. | - The gates should be replaced by one 900 gate with a 500 hinged side panel. The 60 step should be bevelled at 1:10. |
| - The intercom and security keypad outside the gates were too high at 1400. | - The units should be lowered to 1200. |
| - The M and F toilets on the GF were not accessible because of steps down to the doors, standard cubicles and no space for paraplegic facilities. | - A 1:10 ramp could be installed, and paraplegic facilities installed. |
| - The 3 lecture rooms on the GF were accessible. | - None. |
| - The two lecture rooms and six offices on the First Floor were not accessible as there was no lift. | - None at present. |

END